Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

Modified by MSU Physical Plant / Engineering and Architectural Services

SECTION 210500 - COMMON WORK RESULTS FOR FIRE SUPPRESSION

1. GENERAL
	* + 1. RELATED DOCUMENTS
				1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.
			2. SUMMARY
				1. This Section includes the following:

Piping materials and installation instructions common to most piping systems.

Mechanical sleeve seals.

Sleeves.

Escutcheons.

Grout.

Fire-suppression equipment and piping demolition.

Equipment installation requirements common to equipment sections.

* + - 1. DEFINITIONS
				1. Finished Spaces: Spaces other than mechanical and electrical equipment rooms, furred spaces, pipe chases, unheated spaces immediately below roof, spaces above ceilings, unexcavated spaces, crawlspaces, and tunnels.
				2. Exposed, Interior Installations: Exposed to view indoors. Examples include finished occupied spaces and mechanical equipment rooms.
				3. Exposed, Exterior Installations: Exposed to view outdoors or subject to outdoor ambient temperatures and weather conditions. Examples include rooftop locations.
				4. Concealed, Interior Installations: Concealed from view and protected from physical contact by building occupants. Examples include above ceilings and in chases.
				5. Concealed, Exterior Installations: Concealed from view and protected from weather conditions and physical contact by building occupants but subject to outdoor ambient temperatures. Examples include installations within unheated shelters.
			2. SUBMITTALS
				1. Product Data: For the following:

Mechanical sleeve seals.

* + - 1. QUALITY ASSURANCE
				1. Electrical Characteristics for Fire-Suppression Equipment: Equipment of higher electrical characteristics may be furnished provided such proposed equipment is approved in writing and connecting electrical services, circuit breakers, and conduit sizes are appropriately modified. If minimum energy ratings or efficiencies are specified, equipment shall comply with requirements.
			2. DELIVERY, STORAGE, AND HANDLING
				1. Deliver pipes and tubes with factory-applied end caps. Maintain end caps through shipping, storage, and handling to prevent pipe end damage and to prevent entrance of dirt, debris, and moisture.
			3. COORDINATION
				1. Arrange for pipe spaces, chases, slots, and openings in building structure during progress of construction, to allow for fire-suppression installations.
				2. Coordinate installation of required supporting devices and set sleeves in poured-in-place concrete and other structural components as they are constructed.
				3. Coordinate requirements for access panels and doors for fire-suppression items requiring access that are concealed behind finished surfaces. Access panels and doors are specified in Division 08 Section "Access Doors and Frames."
				4. Coordinate systems shutdown (water, fire protection, hot water heating, steam, chilled water, etc.) with MSU Project Manager/MSU Project Representative. Activation and shut down of existing systems shall be conducted by MSU personnel only.
1. PRODUCTS
	* + 1. PIPE, TUBE, AND FITTINGS
				1. Refer to individual Division 21 piping Sections for pipe, tube, and fitting materials and joining methods.
				2. Pipe Threads: ASME B1.20.1 for factory-threaded pipe and pipe fittings.
			2. JOINING MATERIALS
				1. Refer to individual Division 21 piping Sections for special joining materials not listed below.
				2. Pipe-Flange Gasket Materials: Suitable for chemical and thermal conditions of piping system contents.

ASME B16.21, nonmetallic, flat, asbestos-free, 1/8-inch (3.2-mm) maximum thickness unless thickness or specific material is indicated.

Full-Face Type: For flat-face, Class 125, cast-iron and cast-bronze flanges.

Narrow-Face Type: For raised-face, Class 250, cast-iron and steel flanges.

AWWA C110, rubber, flat face, 1/8 inch (3.2 mm) thick, unless otherwise indicated; and full-face or ring type, unless otherwise indicated.

* + - * 1. Flange Bolts and Nuts: ASME B18.2.1, carbon steel, unless otherwise indicated.
				2. Welding Filler Metals: Comply with AWS D10.12 for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.
			1. MECHANICAL SLEEVE SEALS
				1. Description: Modular sealing element unit, designed for field assembly, to fill annular space between pipe and sleeve.

Manufacturers:

Link-Seal.

Metraflex Co.

Sealing Elements: EPDM interlocking links shaped to fit surface of pipe. Include type and number required for pipe material and size of pipe.

Pressure Plates: Carbon steel. Include two for each sealing element.

Connecting Bolts and Nuts: Carbon steel with corrosion-resistant coating of length required to secure pressure plates to sealing elements. Include one for each sealing element.

* + - 1. SLEEVES
				1. Steel Pipe: ASTM A 53, Type E, Grade B, Schedule 40, galvanized, plain ends.
				2. Cast Iron: Cast or fabricated "wall pipe" equivalent to ductile-iron pressure pipe, with plain ends and integral waterstop, unless otherwise indicated.
			2. ESCUTCHEONS
				1. Description: Plastic wall and ceiling escutcheons, with an ID to closely fit around pipe and an OD that completely covers opening.
			3. GROUT
				1. Description: ASTM C 1107, Grade B, nonshrink and nonmetallic, dry hydraulic-cement grout.

Characteristics: Post-hardening, volume-adjusting, nonstaining, noncorrosive, nongaseous, and recommended for interior and exterior applications.

Design Mix: 5000-psi (34.5-MPa), 28-day compressive strength.

Packaging: Premixed and factory packaged.

1. EXECUTION
	* + 1. FIRE-SUPPRESSION DEMOLITION

Delete this Article if no fire-suppression demolition is required. Edit this Article as required for fire-suppression demolition. Show items for demolition on Drawings and supplement Drawings with descriptions in this Article.

* + - * 1. Refer to Division 01 Section "Cutting and Patching" and Division 02 Section "Selective Structure Demolition" for general demolition requirements and procedures.
				2. Disconnect, demolish, and remove fire-suppression systems, equipment, and components indicated to be removed.

Piping to Be Removed: Remove portion of piping indicated to be removed and cap or plug remaining piping with same or compatible piping material.

Piping to Be Abandoned in Place: Drain piping and cap or plug piping with same or compatible piping material.

Equipment to Be Removed: Disconnect and cap services and remove equipment.

Equipment to Be Removed and Reinstalled: Disconnect and cap services and remove, clean, and store equipment; when appropriate, reinstall, reconnect, and make equipment operational.

Equipment to Be Removed and Salvaged: Disconnect and cap services and remove equipment and deliver to Owner.

* + - * 1. If pipe, insulation, or equipment to remain is damaged in appearance or is unserviceable, remove damaged or unserviceable portions and replace with new products of equal capacity and quality.
			1. PIPING SYSTEMS - COMMON REQUIREMENTS
				1. Install piping according to the following requirements and Division 21 Sections specifying piping systems.
				2. Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems. Indicated locations and arrangements were used to size pipe and calculate friction loss, expansion, pump sizing, and other design considerations. Install piping as indicated unless deviations to layout are approved on Coordination Drawings.
				3. Install piping in concealed locations, unless otherwise indicated and except in equipment rooms and service areas.
				4. Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls. Diagonal runs are prohibited unless specifically indicated otherwise.
				5. Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.
				6. Install piping to permit valve servicing.
				7. Install piping at indicated slopes.
				8. Install piping free of sags and bends.
				9. Install fittings for changes in direction and branch connections.
				10. Do not route piping through transformer vaults or above transformers, panelboards, or switchboards, including the required service space for this equipment, unless the piping is serving this equipment.
				11. Select system components with pressure rating equal to or greater than system operating pressure.
				12. Install escutcheons for penetrations of walls and ceilings. Paint escutcheons to match the adjoining wall or ceiling.
				13. Install sleeves for pipes passing through concrete and masonry walls and concrete floor and roof slabs.

Sleeves placed in floors shall be flush with the ceiling and shall have planed, square ends, extending 2 inches above the finished floor, unless otherwise specified or detailed.

Where sleeves pass through reinforced concrete floors, they shall be properly set in position before the concrete is poured, and shall be maintained in position by the Contractor until the concrete is set.

Sleeves placed in concrete beams shall be flush with the side of the beam and large enough to accommodate the bare pipe only. All other sleeves shall be of adequate size to accommodate pipe insulation undiminished in size.

Pipes passing through above grade floor slabs and masonry walls shall have the space between the pipe or insulation and the sleeve packed with non-asbestos wicking or other suitable, approved, non-combustible material.

Pipes passing through walls of Mechanical Equipment Rooms shall be made gas-tight by caulking the space between the pipe and sleeve with a fiber saturated with an approved type of plastic material.

Install sleeves in new walls and slabs as new walls and slabs are constructed.

Except for underground wall penetrations, seal annular space between sleeve and pipe or pipe insulation, using joint sealants appropriate for size, depth, and location of joint. Refer to Division 07 Section "Joint Sealants" for materials and installation.

* + - * 1. Aboveground, Exterior-Wall Pipe Penetrations: Seal penetrations using sleeves and mechanical sleeve seals. Select sleeve size to allow for 1-inch (25-mm) annular clear space between pipe and sleeve for installing mechanical sleeve seals.

Install steel pipe for sleeves smaller than 6 inches (150 mm) in diameter.

Install cast-iron "wall pipes" for sleeves 6 inches (150 mm) and larger in diameter.

Mechanical Sleeve Seal Installation: Select type and number of sealing elements required for pipe material and size. Position pipe in center of sleeve. Assemble mechanical sleeve seals and install in annular space between pipe and sleeve. Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.

* + - * 1. Underground, Exterior-Wall Pipe Penetrations: Install cast-iron "wall pipes" for sleeves. Seal pipe penetrations using mechanical sleeve seals. Select sleeve size to allow for 1-inch (25-mm) annular clear space between pipe and sleeve for installing mechanical sleeve seals.

Mechanical Sleeve Seal Installation: Select type and number of sealing elements required for pipe material and size. Position pipe in center of sleeve. Assemble mechanical sleeve seals and install in annular space between pipe and sleeve. Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.

* + - * 1. Fire-Barrier Penetrations: Maintain indicated fire rating of walls, partitions, ceilings, and floors at pipe penetrations. Seal pipe penetrations with firestop materials. Refer to Division 07 Section "Penetration Firestopping" for materials.
				2. Verify final equipment locations for roughing-in.
				3. Refer to equipment specifications in other Sections of these Specifications for roughing-in requirements.
			1. PIPING JOINT CONSTRUCTION
				1. Join pipe and fittings according to the following requirements and Division 21 Sections specifying piping systems.
				2. Ream ends of pipes and tubes and remove burrs. Bevel plain ends of steel pipe.
				3. Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.
				4. Threaded Joints: Thread pipe with tapered pipe threads according to ASME B1.20.1. Cut threads full and clean using sharp dies. Ream threaded pipe ends to remove burrs and restore full ID. Join pipe fittings and valves as follows:

Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is specified.

Damaged Threads: Do not use pipe or pipe fittings with threads that are corroded or damaged. Do not use pipe sections that have cracked or open welds.

* + - * 1. Welded Joints: Construct joints according to AWS D10.12, using qualified processes and welding operators according to Part 1 "Quality Assurance" Article.
				2. Flanged Joints: Select appropriate gasket material, size, type, and thickness for service application. Install gasket concentrically positioned. Use suitable lubricants on bolt threads.
			1. CONCRETE BASES
				1. Refer to Division 03 Section "Cast-in-Place Concrete" or "Miscellaneous Cast-in-Place Concrete."
				2. Anchor equipment to concrete base according to equipment manufacturer's written instructions.
			2. ERECTION OF METAL SUPPORTS AND ANCHORAGES
				1. Refer to Division 05 Section "Metal Fabrications" for structural steel.
				2. Cut, fit, and place miscellaneous metal supports accurately in location, alignment, and elevation to support and anchor fire-suppression materials and equipment.
				3. Field Welding: Comply with AWS D1.1.
			3. GROUTING
				1. Mix and install grout for fire-suppression equipment base bearing surfaces, pump and other equipment base plates, and anchors.

END OF SECTION 210500