SECTION 220519 - METERS AND GAGES FOR PLUMBING PIPING

1. GENERAL
	* + 1. RELATED DOCUMENTS
				1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.
			2. SUMMARY
				1. Section Includes:

Liquid-in-glass thermometers.

Thermowells.

Dial-type pressure gages.

Gage attachments.

* + - * 1. Related Sections:

Division 21 Section "Facility Fire-Suppression Water-Service Piping" for fire-protection water-service meters outside the building.

Division 21 fire-suppression piping Sections for fire-protection pressure gages.

Division 22 Section "Facility Water Distribution Piping" for domestic water meters and combined domestic and fire-protection water-service meters outside the building.

Division 22 Section " Domestic Water Piping" for water meters inside the building.

* + - 1. SUBMITTALS
				1. Product Data: For each type of product indicated.
				2. Product Certificates: For each type of meter and gage, from manufacturer.
				3. Operation and Maintenance Data: For meters and gages to include in operation and maintenance manuals.
1. PRODUCTS
	* + 1. LIQUID-IN-GLASS THERMOMETERS
				1. Metal-Case, Industrial-Style, Liquid-in-Glass Thermometers:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Trerice, H. O. Co.

Weiss Instruments, Inc.

Standard: ASME B40.200.

Case: Cast aluminum; 9-inch (229-mm) nominal size unless otherwise indicated.

Case Form: Adjustable angle unless otherwise indicated.

Tube: Glass with magnifying lens and blue or red organic liquid.

Tube Background: Nonreflective aluminum with permanently etched scale markings graduated in deg F (deg C).

Window: Glass or plastic.

Stem: Aluminum and of length to suit installation.

Design for Thermowell Installation: Bare stem.

Connector: 1-1/4 inches (32 mm), with ASME B1.1 screw threads.

Accuracy: Plus or minus 1 percent of scale range or one scale division, to a maximum of 1.5 percent of scale range.

* + - 1. THERMOWELLS

ASME B40.200 uses the following symbols for thermowell materials: "CNR" for copper nickel (90-10), "CUNI" for copper nickel (70-30), "CRES" for corrosion-resistant steel, "NICU" for nickel copper, "ALBR" for aluminum bronze, and "CSA" for steel. Other materials are allowed.

* + - * 1. Thermowells:

Standard: ASME B40.200.

Description: Pressure-tight, socket-type fitting made for insertion into piping tee fitting.

Material for Use with Copper Tubing: CNR or CUNI.

Material for Use with Steel Piping: CRES.

Type: Stepped shank unless straight or tapered shank is indicated.

External Threads: NPS 1/2, NPS 3/4, or NPS 1, (DN 15, DN 20, or NPS 25,) ASME B1.20.1 pipe threads.

Internal Threads: 1/2, 3/4, and 1 inch (13, 19, and 25 mm), with ASME B1.1 screw threads.

Bore: Diameter required to match thermometer bulb or stem.

Insertion Length: Length required to match thermometer bulb or stem.

Lagging Extension: Include on thermowells for insulated piping and tubing.

Bushings: For converting size of thermowell's internal screw thread to size of thermometer connection.

* + - * 1. Heat-Transfer Medium: Mixture of graphite and glycerin.
			1. PRESSURE GAGES
				1. Direct-Mounted, Metal-Case, Dial-Type Pressure Gages:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

AMETEK, Inc.; U.S. Gauge.

Ashcroft Inc.

Trerice, H. O. Co.

Weiss Instruments, Inc.

Standard: ASME B40.100.

Case: Liquid-filled type(s); cast aluminum or drawn steel; 4-1/2-inch (114-mm) nominal diameter.

Pressure-Element Assembly: Bourdon tube unless otherwise indicated.

Pressure Connection: Brass, with NPS 1/4 or NPS 1/2 (DN 8 or DN 15), ASME B1.20.1 pipe threads and bottom-outlet type unless back-outlet type is indicated.

Movement: Mechanical, with link to pressure element and connection to pointer.

Dial: Nonreflective aluminum with permanently etched scale markings graduated in psi (kPa).

Pointer: Dark-colored metal.

Window: Glass or plastic.

Ring: Metal.

Accuracy: Grade A, plus or minus 1 percent of middle half of scale range.

* + - 1. GAGE ATTACHMENTS
				1. Snubbers: ASME B40.100, brass; with NPS 1/4 or NPS 1/2 (DN 8 or DN 15), ASME B1.20.1 pipe threads and piston-type surge-dampening device. Include extension for use on insulated piping.
				2. Valves: Brass ball, with NPS 1/4 or NPS 1/2 (DN 8 or DN 15), ASME B1.20.1 pipe threads.
1. EXECUTION
	* + 1. INSTALLATION
				1. Install thermowells with socket extending one-third of pipe diameter and in vertical position in piping tees.
				2. Install thermowells of sizes required to match thermometer connectors. Include bushings if required to match sizes.
				3. Install thermowells with extension on insulated piping.
				4. Fill thermowells with heat-transfer medium.
				5. Install direct-mounted thermometers in thermowells and adjust vertical and tilted positions.
				6. Install remote-mounted thermometer bulbs in thermowells and install cases on panels; connect cases with tubing and support tubing to prevent kinks. Use minimum tubing length.
				7. Install direct-mounted pressure gages in piping tees with pressure gage located on pipe at the most readable position.
				8. Install remote-mounted pressure gages on panel.
				9. Install valve and snubber in piping for each pressure gage for fluids.
				10. Install test plugs in piping tees.
				11. Install thermometers in the following locations:

Outlet of each water heater.

Inlet of hot water return to cold water supply to water heater.

Outlets of each domestic water heat exchanger.

Inlet and outlet of each domestic hot-water storage tank.

Inlet and outlet of each remote domestic water chiller.

* + - * 1. Install pressure gages in the following locations:

Building water service entrance into building.

Inlet and outlet of each pressure-reducing valve.

Suction and discharge of each domestic water pump.

* + - 1. CONNECTIONS
				1. Install meters and gages adjacent to machines and equipment to allow service and maintenance of meters, gages, machines, and equipment.
			2. ADJUSTING
				1. Adjust faces of meters and gages to proper angle for best visibility.
			3. THERMOMETER SCALE-RANGE SCHEDULE
				1. Scale Range for Domestic Cold-Water Piping: 0 to 100 deg F (Minus 20 to plus 50 deg C).
				2. Scale Range for Domestic Hot-Water Piping: 0 to 250 deg F (0 to 150 deg C).
				3. Scale Range for Domestic Cooled-Water Piping: 0 to 100 deg F (Minus 20 to plus 50 deg C).
			4. PRESSURE-GAGE SCALE-RANGE SCHEDULE
				1. Scale Range for Water Service Piping: 0 to 100 psi (0 to 600 kPa).
				2. Scale Range for Domestic Water Piping: 0 to 160 psi (0 to 1100 kPa).

END OF SECTION 220519