Copyright 2008 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

Modified by MSU Physical Plant / Engineering and Architectural Services

SECTION 221513 - GENERAL-SERVICE COMPRESSED-AIR PIPING

1. GENERAL
   * + 1. RELATED DOCUMENTS
          1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.
       2. SUMMARY
          1. This Section includes piping and related specialties for general-service compressed-air systems operating at 200 psig (1380 kPa) or less.
          2. Related Sections include the following:

Division 22 Section "General-Service Packaged Air Compressors and Receivers" for general-service air compressors and accessories.

* + - 1. DEFINITIONS
         1. High-Pressure Compressed-Air Piping: System of compressed-air piping and specialties operating at pressures between 150 and 200 psig (1035 and 1380 kPa).
         2. Low-Pressure Compressed-Air Piping: System of compressed-air piping and specialties operating at pressures of 150 psig (1035 kPa) or less.
      2. SUBMITTALS
         1. Product Data: For the following:

Dielectric fittings.

Flexible pipe connectors.

Safety valves.

Pressure regulators. Include rated capacities and operating characteristics.

Automatic drain valves.

Filters. Include rated capacities and operating characteristics.

Quick couplings.

Hose assemblies.

* + - 1. QUALITY ASSURANCE
         1. Brazing: Qualify processes and operators according to ASME Boiler and Pressure Vessel Code: Section IX, "Welding and Brazing Qualifications," or to AWS B2.2, "Standard for Brazing Procedure and Performance Qualification."
         2. ASME Compliance:

Comply with ASME B31.1, "Power Piping," for high-pressure compressed-air piping.

Comply with ASME B31.9, "Building Services Piping," for low-pressure compressed-air piping.

* + - 1. PROJECT CONDITIONS

Retain this Article if interruption of existing compressed-air service is required.

* + - * 1. Interruption of Existing Compressed-Air Service: Do not interrupt compressed-air service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary compressed-air service according to requirements indicated:

Notify Owner no fewer than two days in advance of proposed interruption of compressed-air service.

Do not proceed with interruption of compressed-air service without Owner's written permission.

1. PRODUCTS
   * + 1. PIPES, TUBES, AND FITTINGS
          1. Schedule 40, Steel Pipe: ASTM A 53/A 53M, Type E or S, Grade B, black or hot-dip zinc coated with ends threaded according to ASME B1.20.1.

Steel Nipples: ASTM A 733, made of ASTM A 53/A 53M or ASTM A 106, Schedule 40, galvanized seamless steel pipe. Include ends matching joining method.

Malleable-Iron Fittings: ASME B16.3, Class 150 or 300, threaded.

Malleable-Iron Unions: ASME B16.39, Class 150 or 300, threaded.

Steel Flanges: ASME B16.5, Class 150 or 300, carbon steel, threaded.

Wrought-Steel Butt-Welding Fittings: ASME B16.9, Schedule 40.

Steel Flanges: ASME B16.5, Class 150 or 300, carbon steel.

Grooved-End Fittings and Couplings:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Anvil International, Inc.

Grinnell.

Victaulic Company.

Grooved-End Fittings: ASTM A 47/A 47M, malleable-iron castings or ASTM A 536, ductile-iron casting; with grooves according to AWWA C606 and dimensions matching steel pipe.

Couplings: AWWA C606 or UL 213, for steel-pipe dimensions and rated for 300-psig (2070-kPa) minimum working pressure. Include ferrous housing sections, gasket suitable for compressed air, and bolts and nuts. Provide EDPM gaskets for oil-free compressed air. Provide NBR gaskets if compressed air contains oil or oil vapor.

* + - * 1. Copper Tube: ASTM B 88, Type K or L (ASTM B 88M, Type A or B) seamless, drawn-temper, water tube.

Wrought-Copper Fittings: ASME B16.22, solder-joint pressure type or MSS SP-73, wrought copper with dimensions for brazed joints.

Cast-Copper-Alloy Flanges: ASME B16.24, Class 150 or 300.

Copper Unions: ASME B16.22 or MSS SP-123.

Grooved-End Fittings and Couplings:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Anvil International, Inc.

Grinnell.

Victaulic Company.

Grooved-End Fittings: ASTM B 75 (ASTM B 75M), copper tube or ASTM B 584, bronze castings.

Couplings: Copper-tube dimensions and design similar to AWWA C606. Include ferrous housing sections, gasket suitable for compressed air, and bolts and nuts. Provide EDPM gasket for oil-free compressed air. Provide NBR gasket if compressed air contains oil or oil vapor.

* + - * 1. Transition Couplings for Metal Piping: Metal coupling or other manufactured fitting same size as, with pressure rating at least equal to and ends compatible with, piping to be joined.
      1. JOINING MATERIALS
         1. Pipe-Flange Gasket Materials: Suitable for compressed-air piping system contents.

ASME B16.21, nonmetallic, flat, asbestos free, 1/8-inch (3.2-mm) maximum thickness unless thickness or specific material is indicated.

Full-Face Type: For flat-face, Class 125, cast-iron and cast-bronze flanges.

Narrow-Face Type: For raised-face, Class 250, cast-iron and steel flanges.

* + - * 1. Flange Bolts and Nuts: ASME B18.2.1, carbon steel, unless otherwise indicated.
        2. Solder Filler Metals: ASTM B 32, lead-free alloys. Include water-flushable flux according to ASTM B 813.
        3. Brazing Filler Metals: AWS A5.8/A5.8M, BCuP Series, copper-phosphorus alloys for general-duty brazing, unless otherwise indicated.
      1. VALVES
         1. Metal Ball, Butterfly, Check, Gate, and Globe Valves: Comply with requirements in Division 22 Section "General-Duty Valves for Plumbing Piping."
      2. DIELECTRIC FITTINGS
         1. General Requirements: Assembly of copper alloy and ferrous materials with separating nonconductive insulating material. Include end connections compatible with pipes to be joined.
         2. Dielectric Unions:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Central Plastics Company.

Watts Regulator Co.; a division of Watts Water Technologies, Inc.

Wilkins; a Zurn company.

Description:

Standard: ASSE 1079.

Revise pressure rating and temperature in first subparagraph below to suit Project, or insert other options for specific applications.

Pressure Rating: 250 psig (1725 kPa).

End Connections: Solder-joint copper alloy and threaded ferrous.

Flanges in first paragraph below are available in at least NPS 1-1/2 to NPS 4 (DN 40 to DN 100).

* + - * 1. Dielectric Flanges:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Central Plastics Company.

Watts Regulator Co.; a division of Watts Water Technologies, Inc.

Wilkins; a Zurn company.

Description:

Standard: ASSE 1079.

Factory-fabricated, bolted, companion-flange assembly.

Revise pressure rating in first subparagraph below to suit Project, or insert other options for specific applications.

Pressure Rating: 300 psig (2070 kPa).

End Connections: Solder-joint copper alloy and threaded ferrous; threaded solder-joint copper alloy and threaded ferrous.

Flanges in paragraph below are available in at least NPS 1/2 to NPS 48 (DN 15 to DN 1200).

* + - * 1. Dielectric-Flange Insulating Kits:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Advance Products & Systems, Inc.

Central Plastics Company.

Description:

Nonconducting materials for field assembly of companion flanges.

Revise pressure rating in first subparagraph below to suit Project, or insert other options for specific applications.

Pressure Rating: 150 psig (1035 kPa).

Gasket: Neoprene or phenolic.

Bolt Sleeves: Phenolic or polyethylene.

Washers: Phenolic with steel backing washers.

* + - 1. FLEXIBLE PIPE CONNECTORS
         1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Flex-Hose Co., Inc.

Hyspan Precision Products, Inc.

Metraflex, Inc.

Universal Metal Hose; a Hyspan Company

* + - * 1. Bronze-Hose Flexible Pipe Connectors: Corrugated-bronze tubing with bronze wire-braid covering and ends brazed to inner tubing.

Working-Pressure Rating: 200 psig (1380 kPa) minimum.

End Connections, NPS 2 (DN 50) and Smaller: Threaded copper pipe or plain-end copper tube.

End Connections, NPS 2-1/2 (DN 65) and Larger: Flanged copper alloy.

* + - * 1. Stainless-Steel-Hose Flexible Pipe Connectors: Corrugated-stainless-steel tubing with stainless-steel wire-braid covering and ends welded to inner tubing.

Working-Pressure Rating: 200 psig (1380 kPa) minimum.

End Connections, NPS 2 (DN 50) and Smaller: Threaded steel pipe nipple.

End Connections, NPS 2-1/2 (DN 65) and Larger: Flanged steel nipple.

* + - 1. SPECIALTIES
         1. Safety Valves: ASME Boiler and Pressure Vessel Code: Section VIII, "Pressure Vessels," construction; National Board certified, labeled, and factory sealed; constructed of bronze body with poppet-type safety valve for compressed-air service.

Pressure Settings: Higher than discharge pressure and same or lower than receiver pressure rating.

* + - * 1. Air-Main Pressure Regulators: Bronze body, direct acting, spring-loaded manual pressure-setting adjustment, and rated for 250-psig (1725-kPa) inlet pressure, unless otherwise indicated.

Type: Pilot operated.

* + - * 1. Air-Line Pressure Regulators: Diaphragm or pilot operated, bronze body, direct acting, spring-loaded manual pressure-setting adjustment, and rated for 200-psig (1380-kPa) minimum inlet pressure, unless otherwise indicated.
        2. Automatic Drain Valves: Stainless-steel body and internal parts, rated for 200-psig (1380-kPa) minimum working pressure, capable of automatic discharge of collected condensate.  Include mounting bracket if wall mounting is indicated.
        3. Coalescing Filters: Coalescing type with activated carbon capable of removing water and oil aerosols; with color-change dye to indicate when carbon is saturated and warning light to indicate when selected maximum pressure drop has been exceeded.  Include mounting bracket if wall mounting is indicated.
        4. Mechanical Filters: Two-stage, mechanical-separation-type, air-line filters. Equip with deflector plates, resin-impregnated-ribbon-type filters with edge filtration, and drain cock.  Include mounting bracket if wall mounting is indicated.

Retain paragraph and subparagraph below if oil feed is required in compressed air for air-operated valve, cylinder, or tool lubrication. Show capacities of lubricators on Drawings.

* + - * 1. Air-Line Lubricators: With drip chamber and sight dome for observing oil drop entering air stream; with oil-feed adjustment screw and quick-release collar for easy bowl removal.  Include mounting bracket if wall mounting is indicated.

Provide with automatic feed device for supplying oil to lubricator.

* + - 1. QUICK COUPLINGS
         1. General Requirements for Quick Couplings: Assembly with locking-mechanism feature for quick connection and disconnection of compressed-air hose.

Retain one or both paragraphs and associated subparagraphs below. Show location of each type on Drawings if both types of quick couplings are required.

* + - * 1. Automatic-Shutoff Quick Couplings: Straight-through brass body with O-ring or gasket seal and stainless-steel or nickel-plated-steel operating parts.

Socket End: With one-way valve and threaded inlet for connection to piping or threaded hose fitting.

Check-valve plug end in first option in subparagraph below is recommended for safety but is not available from all manufacturers.

Plug End: Flow-sensor-bleeder, check-valve or straight-through type with barbed outlet for attaching hose.

* + - * 1. Valveless Quick Couplings: Straight-through brass body with stainless-steel or nickel-plated-steel operating parts.

Socket End: With O-ring or gasket seal, without valve, and with barbed inlet for attaching hose.

Plug End: With barbed outlet for attaching hose.

* + - 1. HOSE ASSEMBLIES
         1. Description: Compatible hose, clamps, couplings, and splicers suitable for compressed-air service, of nominal diameter indicated, and rated for 300-psig (2070-kPa) minimum working pressure, unless otherwise indicated.

Hose: Reinforced single- or double-wire-braid, CR-covered hose for compressed-air service.

Hose Clamps: Stainless-steel clamps or bands.

Hose Couplings: Two-piece, straight-through, threaded brass or stainless-steel O-ring or gasket-seal swivel coupling with barbed ends for connecting two sections of hose.

Hose Splicers: One-piece, straight-through brass or stainless-steel fitting with barbed ends for connecting two sections of hose.

1. EXECUTION
   * + 1. PIPING APPLICATIONS

Delete paragraph and subparagraphs below if receivers are factory packaged with air compressors.

Retain "one of" option in paragraph below to allow Contractor to select piping materials from those retained. Piping materials below are rated for at least 200 psig (1380 kPa).

* + - * 1. Compressed-Air Piping between Air Compressors and Receivers: Use one of the following piping materials for each size range:

NPS 2 (DN 50) and Smaller: Schedule 40, galvanized-steel pipe; threaded, malleable-iron fittings; and threaded joints.

NPS 2 (DN 50) and Smaller: Type K or L (Type A or B), copper tube; wrought-copper fittings; and brazed joints.

NPS 2-1/2 (DN 65) and Larger: Schedule 40, galvanized-steel pipe; threaded, malleable-iron fittings; and threaded joints.

NPS 2-1/2 (DN 65) and Larger: Schedule 40, galvanized-steel pipe; grooved-end fittings; couplings; and grooved joints.

Retain "one of" option in paragraph below to allow Contractor to select piping materials from those retained.

* + - * 1. Low-Pressure Compressed-Air Distribution Piping: Use one of the following piping materials for each size range:

NPS 2 (DN 50) and Smaller: Schedule 40, galvanized-steel pipe; threaded, malleable-iron fittings; and threaded joints.

NPS 2 (DN 50) and Smaller: Type K or L (Type A or B), copper tube; wrought-copper fittings; and brazed or soldered joints.

NPS 2-1/2 (DN 65) and Larger: Schedule 40, galvanized-steel pipe; threaded, malleable-iron fittings; and threaded joints.

NPS 2-1/2 (DN 65) and Larger: Schedule 40, galvanized-steel pipe; grooved-end fittings; couplings; and grooved joints.

Retain "one of" option in paragraph below to allow Contractor to select piping materials from those retained.

* + - * 1. High-Pressure Compressed-Air Distribution Piping: Use one of the following piping materials for each size range:

NPS 2 (DN 50) and Smaller: Schedule 40, galvanized-steel pipe; threaded, malleable-iron fittings; and threaded joints.

NPS 2 (DN 50) and Smaller: Type K or L (Type A or B), copper tube; wrought-copper fittings; and brazed or soldered joints.

NPS 2-1/2 (DN 65) and Larger: Schedule 40, galvanized-steel pipe; threaded, malleable-iron fittings; and threaded joints.

NPS 2-1/2 (DN 65) and Larger: Schedule 40, galvanized-steel pipe; grooved-end fittings; couplings; and grooved joints.

* + - * 1. Drain Piping: Use the following piping materials:

NPS 2 (DN 50) and Smaller: Type L (Type B), copper tube; wrought-copper fittings; and brazed or soldered joints.

* + - 1. VALVE APPLICATIONS
         1. General-Duty Valves: Comply with requirements in Division 22 Section "General-Duty Valves for Plumbing Piping" for metal general-duty valves. Use metal valves, unless otherwise indicated.

Metal General-Duty Valves: Use valve types specified in "Valve Applications" Article in Division 22 Section "General-Duty Valves for Plumbing Piping" according to the following:

Low-Pressure Compressed Air: Valve types specified for low-pressure compressed air.

High-Pressure Compressed Air: Valve types specified for medium-pressure compressed air.

Equipment Isolation NPS 2 (DN 50) and Smaller: Safety-exhaust, copper-alloy ball valve with exhaust vent and pressure rating at least as great as piping system operating pressure.

Grooved-end valves may be used with grooved-end piping and grooved joints.

* + - 1. PIPING INSTALLATION
         1. Refer to Division 22 Section “Common Work Results for Plumbing” for basic installation requirements.
         2. Drawing plans, schematics, and diagrams indicate general location and arrangement of compressed-air piping. Indicated locations and arrangements were used to size pipe and calculate friction loss, expansion, air-compressor sizing, and other design considerations. Install piping as indicated unless deviations to layout are approved on Coordination Drawings.
         3. Install piping adjacent to equipment and machines to allow service and maintenance.
         4. Install air and drain piping with 1 percent slope downward in direction of flow.
         5. Install nipples, flanges, unions, transition and special fittings, and valves with pressure ratings same as or higher than system pressure rating, unless otherwise indicated.
         6. Equipment and Specialty Flanged Connections:

Use steel companion flange with gasket for connection to steel pipe.

Use cast-copper-alloy companion flange with gasket and brazed or soldered joint for connection to copper tube. Do not use soldered joints for connection to air compressors or to equipment or machines producing shock or vibration.

* + - * 1. Flanged joints may be used instead of specified joint for any piping or tubing system.
        2. Install eccentric reducers where compressed-air piping is reduced in direction of flow, with bottoms of both pipes and reducer fitting flush.
        3. Install branch connections to compressed-air mains from top of main. Provide drain leg and drain trap at end of each main and branch and at low points.
        4. Install thermometer and pressure gage on discharge piping from each air compressor and on each receiver. Comply with requirements in Division 22 Section "Meters and Gages for Plumbing Piping."
      1. JOINT CONSTRUCTION
         1. Flanged Joints: Use asbestos-free, nonmetallic gasket suitable for compressed air. Join flanges with gasket and bolts according to ASME B31.9 for bolting procedure.
         2. Grooved Joints: Assemble couplings with housing, gasket, lubricant, and bolts. Join according to AWWA C606 for grooved joints. Do not apply lubricant to prelubricated gaskets.
         3. Dissimilar Metal Piping Material Joints: Use dielectric fittings.
      2. VALVE INSTALLATION
         1. General-Duty Valves: Comply with requirements in Division 22 Section "General-Duty Valves for Plumbing Piping."
         2. Install shutoff valves and unions or flanged joints at compressed-air piping to air compressors.
         3. Install shutoff valve at inlet to each automatic drain valve, filter, lubricator, and pressure regulator.
         4. Install check valves to maintain correct direction of compressed-air flow to and from compressed-air piping specialties and equipment.
      3. DIELECTRIC FITTING INSTALLATION
         1. Install dielectric fittings in piping at connections of dissimilar metal piping and tubing.

Fittings in paragraph below are available in NPS 2 (DN 50) and smaller.

* + - * 1. NPS 2 (DN 50) and Smaller: Use dielectric unions.

Fittings in paragraph below are typically available in NPS 2-1/2 to NPS 4 (DN 65 to DN 100). At least one manufacturer makes larger sizes.

* + - * 1. NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Use dielectric flanges.

Kits in paragraph below are available in NPS 1/2 (DN 15) and larger.

* + - * 1. NPS 5 (DN 125)and Larger: Use dielectric flange kits.
      1. FLEXIBLE PIPE CONNECTOR INSTALLATION
         1. Install flexible pipe connectors in discharge piping of each air compressor.
         2. Install bronze-hose flexible pipe connectors in copper compressed-air tubing.
         3. Install stainless-steel-hose flexible pipe connectors in steel compressed-air piping.
      2. SPECIALTY INSTALLATION
         1. Install safety valves on receivers in quantity and size to relieve at least the capacity of connected air compressors.
         2. Install air-main pressure regulators in compressed-air piping at or near air compressors.
         3. Install air-line pressure regulators in branch piping to equipment and tools.
         4. Install automatic drain valves on aftercoolers, receivers, and dryers. Discharge condensate onto nearest floor drain.
         5. Install coalescing filters in compressed-air piping at or near air compressors and upstream from mechanical filters.  Mount on wall at locations indicated.
         6. Install mechanical filters in compressed-air piping at or near air compressors and downstream from coalescing filters.  Mount on wall at locations indicated.
         7. Install air-line lubricators in branch piping to machine tools.  Mount on wall at locations indicated.
         8. Install quick couplings at piping terminals for hose connections.
         9. Install hose assemblies at hose connections.
      3. CONNECTIONS
         1. Install unions, in piping NPS 2 (DN 50) and smaller, adjacent to each valve and at final connection to each piece of equipment and machine.
         2. Install flanges, in piping NPS 2-1/2 (DN 65) and larger, adjacent to flanged valves and at final connection to each piece of equipment and machine.
      4. HANGER AND SUPPORT INSTALLATION
         1. Comply with requirements in Division 22 Section "Hangers and Supports for Plumbing Piping and Equipment" for pipe hanger and support devices.
         2. Vertical Piping: MSS Type 8 or 42, clamps.
         3. Individual, Straight, Horizontal Piping Runs:

100 Feet (30 m) or Less: MSS Type 1, adjustable, steel clevis hangers.

Longer Than 100 Feet (30 m): MSS Type 43, adjustable roller hangers.

* + - * 1. Multiple, Straight, Horizontal Piping Runs 100 Feet (30 m) or Longer: MSS Type 44, pipe rolls. Support pipe rolls on trapeze.
        2. Base of Vertical Piping: MSS Type 52, spring hangers.
        3. Support horizontal piping within 12 inches (300 mm) of each fitting and coupling.
        4. Rod diameter may be reduced 1 size for double-rod hangers, with 3/8-inch (10-mm) minimum rods.

Maximum spans in two paragraphs and associated subparagraphs below were taken from MSS SP-69 for steel pipe and vapor service.

* + - * 1. Install hangers for Schedule 40, steel piping with the following maximum horizontal spacing and minimum rod diameters:

NPS 1/4 to NPS 1/2 (DN 8 to DN 15): 96 inches (2400 mm) with 3/8-inch (10-mm) rod.

NPS 3/4 to NPS 1-1/4 (DN 20 to DN 32): 84 inches (2100 mm) with 3/8-inch (10-mm) rod.

NPS 1-1/2 (DN 40): 12 feet (3.7 m) with 3/8-inch (10-mm) rod.

NPS 2 (DN 50): 13 feet (4 m) with 3/8-inch (10-mm) rod.

NPS 2-1/2 (DN 65): 14 feet (4.3 m) with 1/2-inch (13-mm) rod.

NPS 3 (DN 80): 15 feet (4.6 m) with 1/2-inch (13-mm) rod.

NPS 3-1/2 (DN 90): 16 feet (4.9 m) with 1/2-inch (13-mm) rod.

NPS 4 (DN 100): 17 feet (5.2 m) with 5/8-inch (16-mm) rod.

NPS 5 (DN 125): 19 feet (5.8 m) with 5/8-inch (16-mm) rod.

NPS 6 (DN 150): 21 feet (6.4 m) with 3/4-inch (19-mm) rod.

NPS 8 (DN 200): 24 feet (7.3 m) with 3/4-inch (19-mm) rod.

NPS 10 (DN 250): 26 feet (7.9 m) with 7/8-inch (22-mm) rod.

NPS 12 (DN 300): 30 feet (9.1 m) with 7/8-inch (22-mm) rod.

* + - * 1. Install supports for vertical, Schedule 40, steel piping every 15 feet (4.6 m).

Maximum spans in two paragraphs and associated subparagraphs below were taken from MSS SP-69 for copper tube and vapor service.

* + - * 1. Install hangers for copper tubing with the following maximum horizontal spacing and minimum rod diameters:

NPS 1/4 (DN 8): 60 inches (1500 mm) with 3/8-inch (10-mm) rod.

NPS 3/8 and NPS 1/2 (DN 10 and DN 15): 72 inches (1800 mm) with 3/8-inch (10-mm) rod.

NPS 3/4 (DN 20): 84 inches (2100 mm) with 3/8-inch (10-mm) rod.

NPS 1 (DN 25): 96 inches (2400 mm) with 3/8-inch (10-mm) rod.

NPS 1-1/4 (DN 32): 108 inches (2700 mm) with 3/8-inch (10-mm) rod.

NPS 1-1/2 (DN 40): 10 feet (3 m) with 3/8-inch (10-mm) rod.

NPS 2 (DN 50): 11 feet (3.4 m) with 3/8-inch (10-mm) rod.

NPS 2-1/2 (DN 65): 13 feet (4 m) with 1/2-inch (13-mm) rod.

NPS 3 (DN 80): 14 feet (4.3 m) with 1/2-inch (13-mm) rod.

NPS 3-1/2 (DN 90): 15 feet (4.6 m) with 1/2-inch (13-mm) rod.

NPS 4 (DN 100): 16 feet (4.9 m) with 1/2-inch (13-mm) rod.

NPS 5 (DN 125): 18 feet (5.5 m) with 1/2-inch (13-mm) rod.

NPS 6 (DN 150): 20 feet (6 m) with 5/8-inch (16-mm) rod.

NPS 8 (DN 200): 23 feet (7 m) with 3/4-inch (19-mm) rod.

* + - * 1. Install supports for vertical copper tubing every 10 feet (3 m).
      1. LABELING AND IDENTIFICATION
         1. Install identifying labels and devices for general-service compressed-air piping, valves, and specialties. Comply with requirements in Division 22 Section "Identification for Plumbing Piping and Equipment."
      2. FIELD QUALITY CONTROL
         1. Perform field tests and inspections.
         2. Tests and Inspections:

Piping Leak Tests for Metal Compressed-Air Piping: Test new and modified parts of existing piping. Cap and fill general-service compressed-air piping with oil-free dry air or gaseous nitrogen to pressure of 50 psig (345 kPa) above system operating pressure, but not less than 150 psig (1035 kPa). Isolate test source and let stand for four hours to equalize temperature. Refill system, if required, to test pressure; hold for two hours with no drop in pressure.

Repair leaks and retest until no leaks exist.

Inspect filters lubricators and pressure regulators for proper operation.

* + - * 1. Prepare test reports.

END OF SECTION 221513