Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

Modified by MSU Physical Plant / Engineering and Architectural Services

SECTION 224700 - DRINKING FOUNTAINS AND WATER COOLERS

1. GENERAL
   * + 1. RELATED DOCUMENTS
          1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.
       2. SUMMARY
          1. This Section includes the following drinking fountains and water coolers and related components:

Drinking Fountains.

Water coolers.

Fixture supports.

* + - 1. DEFINITIONS
         1. Accessible Drinking Fountain or Water Cooler: Fixture that can be approached and used by people with disabilities.
         2. Drinking Fountain: Fixture with nozzle for delivering stream of water for drinking.
         3. Fitting: Device that controls flow of water into or out of fixture.
         4. Fixture: Drinking fountain or water cooler unless one is specifically indicated.
         5. Remote Water Cooler: Electrically powered equipment for generating cooled drinking water.
         6. Water Cooler: Electrically powered fixture for generating and delivering cooled drinking water.
      2. SUBMITTALS
         1. Product Data: For each fixture indicated. Include rated capacities, furnished specialties, and accessories.
         2. Shop Drawings: Diagram power, signal, and control wiring.
         3. Field quality-control test reports.
         4. Operation and Maintenance Data: For fixtures to include in emergency, operation, and maintenance manuals.
      3. QUALITY ASSURANCE
         1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.
         2. Regulatory Requirements: Comply with requirements in ICC A117.1, "Accessible and Usable Buildings and Facilities"; Public Law 90-480, "Architectural Barriers Act" ; and Public Law 101-336, "Americans with Disabilities Act" ; for fixtures for people with disabilities.
         3. NSF Standard: Comply with NSF 61, "Drinking Water System Components--Health Effects," for fixture materials that will be in contact with potable water.
         4. ARI Standard: Comply with ARI 1010, "Self-Contained, Mechanically Refrigerated Drinking-Water Coolers," for water coolers and with ARI's "Directory of Certified Drinking Water Coolers" for type and style classifications.
         5. ASHRAE Standard: Comply with ASHRAE 34, "Designation and Safety Classification of Refrigerants," for water coolers. Provide HFC 134a (tetrafluoroethane) refrigerant, unless otherwise indicated.

1. PRODUCTS
   * + 1. DRINKING FOUNTAINS
          1. Wall-Mounted Drinking Fountains:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Filtrine Manufacturing Company; Drinking Water Division.

Halsey Taylor.

Haws Corporation; Model 1119.

Oasis Corporation.

Description: Accessible, Hi-Lo wall-mounted.

Material: Type 304, 18 gauge Stainless steel with satin finish.

Receptor Shape: Rectangular.

Back Panel: Stainless-steel satin finish wall plate behind drinking fountain.

Bubblers: Polished chrome-plated brass vandal-resistant bubbler heads.

Control: Push button.

Supply: NPS 3/8 with ball, gate, or globe valve.

Drain: Grid with NPS 1-1/4 minimum horizontal waste and trap complying with ASME A112.18.2.

Support: Hi-LO universal mounting plate.

* + - 1. WATER COOLERS
         1. Electric Water Coolers:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Elkay Manufacturing Co. (Note: Elkay Bottle Fillers Not Allowed)

Halsey Taylor.

Haws Corporation; Model HWBFA8L.VRC

Oasis Corporation.

Description: Hi-Lo, barrier-free, vandal-resistant wall-mounted.

Cabinet: All stainless steel.

Bubbler: One, with adjustable stream regulator, located on deck.

Control: Push button.

Supply: NPS 3/8 with ball, gate, or globe valve.

Filter: One or more water filters complying with NSF 42 and NSF 53 for cyst and lead reduction to below EPA standards; with capacity sized for unit peak flow rate.

Drain: Grid with NPS 1-1/4 minimum horizontal waste and trap complying with ASME A112.18.2.

Cooling System: Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, HFC refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

Capacity: 8 gph of 50 deg F cooled water from 80 deg F inlet water and 90 deg F ambient air temperature.

Electrical Characteristics: 120-V ac; single phase; 60 Hz.

* + - 1. FIXTURE SUPPORTS
         1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Josam Co.

MIFAB Manufacturing, Inc.

Smith, Jay R. Mfg. Co.

Tyler Pipe; Wade Div.

Watts Drainage Products Inc.; a div. of Watts Industries, Inc.

Zurn Plumbing Products Group; Specification Drainage Operation.

* + - * 1. Description: ASME A112.6.1M, water cooler carriers. Include vertical, steel uprights with feet and tie rods and bearing plates with mounting studs matching fixture to be supported.

Type I: Hanger-type carrier with two vertical uprights.

Type II: Bi-level, hanger-type carrier with three vertical uprights.

Supports for Accessible Fixtures: Include rectangular, vertical, steel uprights instead of steel pipe uprights.

1. EXECUTION
   * + 1. EXAMINATION
          1. Examine roughing-in for water and waste piping systems to verify actual locations of piping connections before fixture installation. Verify that sizes and locations of piping and types of supports match those indicated.
          2. Examine walls and floors for suitable conditions where fixtures are to be installed.
          3. Proceed with installation only after unsatisfactory conditions have been corrected.
       2. APPLICATIONS
          1. Use carrier off-floor supports for wall-mounting fixtures, unless otherwise indicated.
          2. Use mounting frames for recessed water coolers, unless otherwise indicated.
          3. Set freestanding and pedestal drinking fountains on floor.
          4. Set remote water coolers on floor, unless otherwise indicated.
          5. Use chrome-plated brass or copper tube, fittings, and valves in locations exposed to view. Plain copper tube, fittings, and valves may be used in concealed locations.
       3. INSTALLATION
          1. Install off-floor supports affixed to building substrate and attach wall-mounting fixtures, unless otherwise indicated.
          2. Install mounting frames affixed to building construction and attach recessed water coolers to mounting frames, unless otherwise indicated.
          3. Install fixtures level and plumb. For fixtures indicated for children, install at height required by authorities having jurisdiction.
          4. Install water-supply piping with shutoff valve on supply to each fixture to be connected to water distribution piping. Use ball valves. Install valves in locations where they can be easily reached for operation. Valves are specified in Division 22 Section "General-Duty Valves for Plumbing Piping."
          5. Install trap and waste piping on drain outlet of each fixture to be connected to sanitary drainage system.
          6. Install pipe escutcheons at wall penetrations in exposed, finished locations. Use deep-pattern escutcheons where required to conceal protruding pipe fittings. Escutcheons are specified in Division 22 Section "Common Work Results for Plumbing."
          7. Seal joints between fixtures and walls and floors using sanitary-type, one-part, mildew-resistant, silicone sealant. Match sealant color to fixture color. Sealants are specified in Division 07 Section "Joint Sealants."
       4. CONNECTIONS
          1. Piping installation requirements are specified in other Division 22 Sections. Drawings indicate general arrangement of piping, fittings, and specialties.
          2. Connect fixtures with water supplies, stops, and risers, and with traps, soil, waste, and vent piping. Use size fittings required to match fixtures.
          3. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."
          4. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."
       5. FIELD QUALITY CONTROL
          1. Water Cooler Testing: After electrical circuitry has been energized, test for compliance with requirements. Test and adjust controls and safeties.

Remove and replace malfunctioning units and retest as specified above.

Report test results in writing.

* + - 1. ADJUSTING
         1. Adjust fixture flow regulators for proper flow and stream height.
         2. Adjust water cooler temperature settings.
      2. CLEANING
         1. After completing fixture installation, inspect unit. Remove paint splatters and other spots, dirt, and debris. Repair damaged finish to match original finish.
         2. Clean fixtures, on completion of installation, according to manufacturer's written instructions.

END OF SECTION 224700