Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

Modified by MSU Physical Plant /Engineering and Architectural Services

SECTION 238233 - CONVECTORS

1. GENERAL
	* + 1. RELATED DOCUMENTS
				1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 01 Specification Sections, apply to this Section.
			2. SUMMARY
				1. This Section includes the following:

Finned-tube radiators.

Convectors.

* + - 1. SUBMITTALS
				1. Product Data: Include rated capacities, operating characteristics, furnished specialties, and accessories for each type of product indicated.
				2. Shop Drawings: Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Location and size of each field connection.

Location and arrangement of piping valves and specialties.

Enclosure joints, corner pieces, access doors, and other accessories.

* + - * 1. Color Samples for Initial Selection: For units with factory-applied color finishes.
				2. Field quality-control test reports.
				3. Operation and Maintenance Data: For convection heating units to include in emergency, operation, and maintenance manuals.
			1. QUALITY ASSURANCE
				1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.
1. PRODUCTS
	* + 1. HOT-WATER OR STEAM FINNED-TUBE RADIATORS
				1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Slant/Fin.

Sterling.

Trane.

Vulcan Radiator; Style DS.

Airtex

* + - * 1. Performance Ratings: Rate finned-tube radiators according to Hydronics Institute's "I=B=R Testing and Rating Standard for Finned-Tube (Commercial) Radiation."
				2. Heating Elements:

Steam: Steel tubing mechanically expanded into flanged collars of evenly spaced steel fins resting on element supports. Tube ends shall be threaded.

Hot-water: Copper tubing mechanically expanded into flanged collars of evenly spaced aluminum fins resting on element supports. Tube ends shall be expanded for soldering.

* + - * 1. Element Supports: Ball-bearing cradle type to permit longitudinal movement on enclosure brackets.
				2. Rust-Resistant Front Panel: Minimum 0.064-inch- (1.6-mm-) thick, ASTM A 653/A 653M, G60 galvanized steel.
				3. Wall-Mounting Back Panel: Minimum 0.0329-inch- (0.85-mm-) thick steel, full height, with full-length channel support for front panel without exposed fasteners.

Retain paragraph above for wall mounting or first paragraph below for floor mounting.

* + - * 1. Floor-Mounting Pedestals: Conceal insulated piping at maximum 36-inch (914-mm) spacing. Pedestal-mounting back panel shall be solid panel matching front panel. Provide stainless-steel escutcheon for floor openings at pedestals.
				2. Support Brackets: Locate at maximum 36-inch (914-mm) spacing to support front panel and element.
				3. Finish: Baked-enamel finish in manufacturer's standard color as selected by Architect.
				4. Damper: Knob-operated internal damper at enclosure outlet.
				5. Access Doors: Factory made, permanently hinged with tamper-resistant fastener, minimum size 6 by 7 inches (150 by 175 mm), integral with enclosure.
				6. Enclosure Style: Sloped top.

Top Outlet Grille: Punched louver; painted to match enclosure.

* + - * 1. Accessories: Filler sections, corners, relay sections, and splice plates all matching the enclosure and grille finishes.
			1. HOT-WATER OR STEAM CONVECTORS
				1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Slant/Fin

Sterling

Trane

Vulcan

ZehnderRittling

* + - * 1. Convector Elements: Seamless copper tubing mechanically expanded into evenly spaced aluminum fins and rolled into cast-iron or brass headers with inlet/outlet and air vent; steel side plates and supports. Factory-pressure-test element at minimum 100 psig (690 kPa).
				2. Front and Top Panel: Minimum 0.0528-inch- (1.35-mm-) thick steel with exposed corners rounded; removable front panels with tamper-resistant fasteners braced and reinforced for stiffness.
				3. Wall-Mounting Back and End Panels: Minimum 0.0428-inch- (1.1-mm-) thick steel.

Retain paragraph above for wall mounting or first paragraph below for floor-mounting.

* + - * 1. Floor-Mounting Pedestals: Conceal conduit for power and control wiring at maximum 36-inch (914-mm) spacing. Pedestal-mounting back panel shall be solid panel matching front panel.
				2. Support Brackets: Locate at maximum 36-inch (914-mm) spacing to support front panel and element.
				3. Insulation: 1/2-inch- (13-mm-) thick, fibrous glass on inside of the back of the enclosure.
				4. Finish: Baked-enamel finish in manufacturer's standard color as selected by Architect.
				5. Damper: Knob-operated internal damper.
				6. Enclosure Style: Sloped top.

Top Outlet Grille: Punched louver; painted to match enclosure.

1. EXECUTION
	* + 1. EXAMINATION
				1. Examine areas to receive convection heating units for compliance with requirements for installation tolerances and other conditions affecting performance.
				2. Examine roughing-in for connections to verify actual locations before convection heating unit installation.
				3. Proceed with installation only after unsatisfactory conditions have been corrected.
			2. FINNED-TUBE RADIATOR INSTALLATION
				1. Install units level and plumb.
				2. Install finned-tube radiators according to Guide 2000 - Residential Hydronic Heating.
				3. Install enclosure continuously around corners, using outside and inside corner fittings.
				4. Join sections with splice plates and filler pieces to provide continuous enclosure.
				5. Install access doors for access to valves.
				6. Install enclosure continuously from wall to wall.
				7. Terminate enclosures with manufacturer's end caps, except where enclosures are indicated to extend to adjoining walls.
				8. Install valves within reach of access door provided in enclosure.
				9. Install air-seal gasket between wall and recessing flanges or front cover of fully recessed unit.
				10. Install piping within pedestals for freestanding units.
			3. CONVECTOR INSTALLATION
				1. Install units level and plumb.
				2. Install valves within reach of access door provided in enclosure.
				3. Install air-seal gasketing between wall and recessing flanges or front cover of fully recessed unit.
				4. Install piping within pedestals for freestanding units.
			4. CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

Retain paragraphs and subparagraphs below for hot-water or steam piping.

* + - * 1. Connect hot-water units and components to piping according to Division 23 Section "Hydronic Piping."

Install shutoff valves on inlet and outlet, and balancing valve on outlet.

* + - * 1. Connect steam units and components to piping according to Division 23 Section "Steam and Condensate Heating Piping."

Install shutoff valve on inlet; install strainer, steam trap, and shutoff valve on outlet.

* + - * 1. Install control valves as required by Division 23 Section "Instrumentation and Control for HVAC."
				2. Install piping adjacent to convection heating units to allow service and maintenance.
				3. Conceal piping behind the enclosure of the finned-tube radiations.
			1. FIELD QUALITY CONTROL
				1. Perform the following field tests and inspections and prepare test reports:

Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

* + - * 1. Remove and replace convection heating units that do not pass tests and inspections and retest as specified above.

END OF SECTION 238233