SECTION 220500 - COMMON WORK RESULTS FOR PLUMBING

1. GENERAL
   * + 1. RELATED DOCUMENTS
          1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.
       2. SUMMARY
          1. This Section includes the following:

Piping materials and installation instructions common to most piping systems.

Mechanical sleeve seals.

Sleeves.

Escutcheons.

Grout.

Plumbing demolition.

Equipment installation requirements common to equipment sections.

Concrete bases.

Supports and anchorages.

* + - 1. DEFINITIONS
         1. Finished Spaces: Spaces other than mechanical and electrical equipment rooms, furred spaces, pipe chases, unheated spaces immediately below roof, spaces above ceilings, unexcavated spaces, crawlspaces, and tunnels.
         2. Exposed, Interior Installations: Exposed to view indoors. Examples include finished occupied spaces and mechanical equipment rooms.
         3. Exposed, Exterior Installations: Exposed to view outdoors or subject to outdoor ambient temperatures and weather conditions. Examples include rooftop locations.
         4. Concealed, Interior Installations: Concealed from view and protected from physical contact by building occupants. Examples include above ceilings and in chases.
         5. Concealed, Exterior Installations: Concealed from view and protected from weather conditions and physical contact by building occupants but subject to outdoor ambient temperatures. Examples include installations within unheated shelters.
         6. The following are industry abbreviations for plastic materials:

CPVC: Chlorinated polyvinyl chloride plastic.

PE: Polyethylene plastic.

PVC: Polyvinyl chloride plastic.

* + - * 1. The following are industry abbreviations for rubber materials:

EPDM: Ethylene-propylene-diene terpolymer rubber.

NBR: Acrylonitrile-butadiene rubber.

* + - 1. SUBMITTALS
         1. Product Data: For the following:

Transition fittings.

Dielectric fittings.

Mechanical sleeve seals.

Escutcheons.

* + - * 1. Welding certificates.
        2. Certificate of Acceptance: Provide certificate as described in this section.
      1. QUALITY ASSURANCE
         1. Steel Support Welding: Qualify processes and operators according to AWS D1.1, "Structural Welding Code--Steel."
         2. Steel Pipe Welding: Qualify processes and operators according to ASME Boiler and Pressure Vessel Code: Section IX, "Welding and Brazing Qualifications."

Comply with provisions in ASME B31 Series, "Code for Pressure Piping."

* + - * 1. Electrical Characteristics for Plumbing Equipment: Equipment of higher electrical characteristics may be furnished provided such proposed equipment is approved in writing and connecting electrical services, circuit breakers, and conduit sizes are appropriately modified. If minimum energy ratings or efficiencies are specified, equipment shall comply with requirements.
        2. Permits and Inspections

The Plumbing Contractor shall obtain and pay for all permits required by the State of Michigan Department of Licensing and Regulatory Affairs, Plumbing Division.

The Plumbing Contractor shall submit, to precede request for final payment, a copy of the Certificate of Acceptance of the plumbing systems.

* + - 1. DELIVERY, STORAGE, AND HANDLING
         1. Deliver pipes and tubes with factory-applied end caps. Maintain end caps through shipping, storage, and handling to prevent pipe end damage and to prevent entrance of dirt, debris, and moisture.
         2. Store plastic pipes protected from direct sunlight. Support to prevent sagging and bending.
      2. COORDINATION
         1. Arrange for pipe spaces, chases, slots, and openings in building structure during progress of construction, to allow for plumbing installations.
         2. Coordinate installation of required supporting devices and set sleeves in poured-in-place concrete and other structural components as they are constructed.
         3. Coordinate requirements for access panels and doors for plumbing items requiring access that are concealed behind finished surfaces. Access panels and doors are specified in Division 08 Section "Access Doors and Frames."
         4. Coordinate systems shutdown (water, fire protection, hot water heating, steam, chilled water, etc.) with MSU Project Manager/MSU Project Representative. Activation and shut down of existing systems shall be conducted by MSU personnel only.

1. PRODUCTS
   * + 1. MANUFACTURERS
          1. Manufacturers: Subject to compliance with requirements, provide products by the manufacturers specified.
       2. PIPE, TUBE, AND FITTINGS
          1. Refer to individual Division 22 piping Sections for pipe, tube, and fitting materials and joining methods.
          2. Pipe Threads: ASME B1.20.1 for factory-threaded pipe and pipe fittings.
       3. JOINING MATERIALS
          1. Refer to individual Division 22 piping Sections for special joining materials not listed below.
          2. Pipe-Flange Gasket Materials: Suitable for chemical and thermal conditions of piping system contents.

ASME B16.21, nonmetallic, flat, asbestos-free, 1/8-inch maximum thickness unless thickness or specific material is indicated.

Full-Face Type: For flat-face, Class 125, cast-iron and cast-bronze flanges.

Narrow-Face Type: For raised-face, Class 250, cast-iron and steel flanges.

AWWA C110, rubber, flat face, 1/8 inch thick, unless otherwise indicated; and full-face or ring type, unless otherwise indicated.

* + - * 1. Flange Bolts and Nuts: ASTM A-354 Grade BD and SAE J-429 Grade 8 for steam and condensate application, and ASTM A-354 and SAE J-429 Grade 5 for other low service temperature applications, unless otherwise indicated.
        2. Solder Filler Metals: ASTM B 32, lead-free alloys, 95/5 tin-copper. Include water-flushable flux according to ASTM B 813.
        3. Brazing Filler Metals: AWS A5.8, BCuP Series, copper-phosphorus alloys for general-duty brazing, unless otherwise indicated; and AWS A5.8, BAg1, silver alloy for refrigerant piping, unless otherwise indicated.
        4. Welding Filler Metals: Comply with AWS D10.12 for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.
        5. Solvent Cements for Joining Plastic Piping:

PVC Piping: ASTM D 2564. Include primer according to ASTM F 656.

CPVC Piping: ASTM F 493.

* + - * 1. Fiberglass Pipe Adhesive: As furnished or recommended by pipe manufacturer.
      1. MECHANICAL SLEEVE SEALS
         1. Description: Modular sealing element unit, designed for field assembly, to fill annular space between pipe and sleeve.

Manufacturers:

Link-Seal.

Metraflex Co.

Sealing Elements: EPDM interlocking links shaped to fit surface of pipe. Include type and number required for pipe material and size of pipe.

Pressure Plates: Carbon steel. Include two for each sealing element.

Connecting Bolts and Nuts: Carbon steel with corrosion-resistant coating of length required to secure pressure plates to sealing elements. Include one for each sealing element.

* + - 1. SLEEVES

Use galvanized steel pipes in kitchen areas only unless directed otherwise.

* + - * 1. Steel Pipe: ASTM A 53, Type E, Grade B, Schedule 40, galvanized, plain ends.
        2. Steel Pipe: ASTM A 53, Type E, Grade B, Schedule 40, plain ends.
      1. ESCUTCHEONS
         1. Description: Manufactured wall and ceiling escutcheons and floor plates, with an ID to closely fit around pipe, tube, and insulation of insulated piping and an OD that completely covers opening.
         2. One-Piece, Deep-Pattern Type: Deep-drawn, box-shaped brass with polished chrome-plated finish.
         3. One-Piece, Cast-Brass Type: With set screw.

Finish: Polished chrome-plated.

* + - * 1. Split-Casting, Cast-Brass Type: With concealed hinge and set screw.

Finish: Polished chrome-plated.

* + - * 1. One-Piece, Floor-Plate Type: Cast-iron floor plate.
        2. Split-Casting, Floor-Plate Type: Cast brass with concealed hinge and set screw.
      1. GROUT
         1. Description: ASTM C 1107, Grade B, nonshrink and nonmetallic, dry hydraulic-cement grout.

Characteristics: Post-hardening, volume-adjusting, nonstaining, noncorrosive, nongaseous, and recommended for interior and exterior applications.

Design Mix: 5000-psi, 28-day compressive strength.

Packaging: Premixed and factory packaged.

1. EXECUTION
   * + 1. PLUMBING DEMOLITION

Delete this Article if no plumbing demolition is required. Edit this Article as required for plumbing demolition. Show items for demolition on Drawings and supplement Drawings with descriptions in this Article.

* + - * 1. Refer to Division 01 Section "Cutting and Patching" and Division 02 Section "Selective Structure Demolition" for general demolition requirements and procedures.
        2. Disconnect, demolish, and remove plumbing systems, equipment, and components indicated to be removed.

Piping to Be Removed: Remove portion of piping indicated to be removed and cap or plug remaining piping with same or compatible piping material.

Piping to Be Abandoned in Place: Drain piping and cap or plug piping with same or compatible piping material.

Equipment to Be Removed: Disconnect and cap services and remove equipment.

Equipment to Be Removed and Reinstalled: Disconnect and cap services and remove, clean, and store equipment; when appropriate, reinstall, reconnect, and make equipment operational.

Equipment to Be Removed and Salvaged: Disconnect and cap services and remove equipment and deliver to Owner.

* + - * 1. If pipe, insulation, or equipment to remain is damaged in appearance or is unserviceable, remove damaged or unserviceable portions and replace with new products of equal capacity and quality.
      1. PIPING SYSTEMS - COMMON REQUIREMENTS
         1. Install piping according to the following requirements and Division 22 Sections specifying piping systems.
         2. Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems. Indicated locations and arrangements were used to size pipe and calculate friction loss, expansion, pump sizing, and other design considerations. Install piping as indicated unless deviations to layout are approved on Coordination Drawings.
         3. Install piping in concealed locations, unless otherwise indicated and except in equipment rooms and service areas.
         4. Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls. Diagonal runs are prohibited unless specifically indicated otherwise.
         5. Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.
         6. Install piping to permit valve servicing.
         7. Install piping at indicated slopes.
         8. Install piping free of sags and bends.
         9. Install fittings for changes in direction and branch connections. T-drill system for mechanically formed tee connections and couplings, and Victaulic hole cut piping system are not allowed.
         10. Install piping to allow application of insulation.
         11. Piping shall not project beyond walls or steel lines nor shall it hang below slabs more than is absolutely necessary. Particular attention shall be paid to the required clearances.
         12. Offset piping where required to avoid interference with other work, to provide greater headroom or clearance, or to conceal pipe more readily. Offsets shall be properly drained or trapped where necessary.
         13. Provide swing joints and expansion bends wherever required to allow the piping to expand without undue stress to connections or equipment.
         14. Isolate pipe from the building construction to prevent transmission of vibration to the structure and to eliminate noise.
         15. Exposed piping around fixtures or in other conspicuous places shall not show tool marks at fittings.
         16. Do not route piping through transformer vaults or above transformers, panelboards, or switchboards, including the required service space for this equipment, unless the piping is serving this equipment.
         17. Select system components with pressure rating equal to or greater than system operating pressure.
         18. Eccentric reducing couplings shall be provided in all cases where air or water pockets would otherwise occur due to a reduction in pipe size. Eccentric couplings shall make the pipe flush on the top for water lines.
         19. Install escutcheons for penetrations of walls, ceilings, and floors according to the following:

New Piping:

Piping with Fitting or Sleeve Protruding from Wall: One-piece, deep-pattern type.

Chrome-Plated Piping: One-piece, cast-brass type with polished chrome-plated finish.

Bare Piping at Wall and Floor Penetrations in Finished Spaces: One-piece, cast-brass type with polished chrome-plated finish.

Bare Piping at Ceiling Penetrations in Finished Spaces: One-piece, cast-brass type with polished chrome-plated finish.

Bare Piping in Unfinished Service Spaces: One-piece, cast-brass type with rough-brass finish.

Bare Piping in Equipment Rooms: One-piece, cast-brass type.

Bare Piping at Floor Penetrations in Equipment Rooms: One-piece, floor-plate type.

Existing Piping: Use the following:

Chrome-Plated Piping: Split-casting, cast-brass type with chrome-plated finish.

Bare Piping at Wall and Floor Penetrations in Finished Spaces: Split-casting, cast-brass type with chrome-plated finish.

Bare Piping at Ceiling Penetrations in Finished Spaces: Split-casting, cast-brass type with chrome-plated finish.

Bare Piping in Unfinished Service Spaces: Split-casting, cast-brass type with rough-brass finish.

Bare Piping in Equipment Rooms: Split-casting, cast-brass type.

Bare Piping at Floor Penetrations in Equipment Rooms: Split-casting, floor-plate type.

* + - * 1. All pipes extending through the roof shall be flashed with six pound lead flashing extending 6 inches beyond the pipe, welded to a lead sleeve extended up around the vent pipes, and rolled over into the pipe.
        2. Install sleeves for pipes passing through concrete and masonry walls and concrete floor and roof slabs.

Sleeves placed in floors shall be flush with the ceiling and shall have planed, square ends, extending 2 inches above the finished floor, unless otherwise specified or detailed.

Where sleeves pass through reinforced concrete floors, they shall be properly set in position before the concrete is poured, and shall be maintained in position by the Contractor until the concrete is set.

Sleeves placed in concrete beams shall be flush with the side of the beam and large enough to accommodate the bare pipe only. All other sleeves shall be of adequate size to accommodate pipe insulation undiminished in size.

Pipes passing through above grade floor slabs and masonry walls shall have the space between the pipe or insulation and the sleeve packed with non-asbestos wicking or other suitable, approved, non-combustible material.

Pipes passing through walls of Mechanical Equipment Rooms shall be made gas-tight by caulking the space between the pipe and sleeve with a fiber saturated with an approved type of plastic material.

* + - * 1. Aboveground, Exterior-Wall Pipe Penetrations: Seal penetrations using sleeves and mechanical sleeve seals. Select sleeve size to allow for 1-inch (25-mm) annular clear space between pipe and sleeve for installing mechanical sleeve seals.

Install steel pipe for sleeves smaller than 6 inches (150 mm) in diameter.

Install cast-iron "wall pipes" for sleeves 6 inches (150 mm) and larger in diameter.

Mechanical Sleeve Seal Installation: Select type and number of sealing elements required for pipe material and size. Position pipe in center of sleeve. Assemble mechanical sleeve seals and install in annular space between pipe and sleeve. Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.

* + - * 1. Underground, Exterior-Wall Pipe Penetrations: Install cast-iron "wall pipes" for sleeves. Seal pipe penetrations using mechanical sleeve seals. Select sleeve size to allow for 1-inch (25-mm) annular clear space between pipe and sleeve for installing mechanical sleeve seals.

Mechanical Sleeve Seal Installation: Select type and number of sealing elements required for pipe material and size. Position pipe in center of sleeve. Assemble mechanical sleeve seals and install in annular space between pipe and sleeve. Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.

* + - * 1. Fire-Barrier Penetrations: Maintain indicated fire rating of walls, partitions, ceilings, and floors at pipe penetrations. Seal pipe penetrations with firestop materials. Refer to Division 07 Section "Penetration Firestopping" for materials.
        2. Verify final equipment locations for roughing-in.
        3. Refer to equipment specifications in other Sections of these Specifications for roughing-in requirements.
        4. Return hot water line shall be no further than 15’ from the fixture needing hot water.
      1. PIPING JOINT CONSTRUCTION
         1. Join pipe and fittings according to the following requirements and Division 22 Sections specifying piping systems.
      2. PIPING CONNECTIONS
         1. Make connections according to the following, unless otherwise indicated:

Install unions, in piping NPS 2 and smaller, adjacent to each valve and at final connection to each piece of equipment.

Install flanges, in piping NPS 2-1/2 and larger, adjacent to flanged valves and at final connection to each piece of equipment.

Dry Piping Systems: Install dielectric unions and flanges to connect piping materials of dissimilar metals.

Wet Piping Systems: Install dielectric coupling and nipple fittings to connect piping materials of dissimilar metals.

* + - * 1. Unions shall be used in preference to couplings where their use will facilitate dismantling the pipe for maintenance.
        2. Install transition couplings at joints of dissimilar piping.
        3. No Uni-flange pipe adapters will be allowed.
      1. EQUIPMENT INSTALLATION - COMMON REQUIREMENTS
         1. Install equipment to allow maximum possible headroom unless specific mounting heights are not indicated.
         2. Install equipment level and plumb, parallel and perpendicular to other building systems and components in exposed interior spaces, unless otherwise indicated.
         3. Install plumbing equipment to facilitate service, maintenance, and repair or replacement of components. Connect equipment for ease of disconnecting, with minimum interference to other installations. Extend grease fittings to accessible locations.
         4. Install equipment to allow right of way for piping installed at required slope.
      2. CONCRETE BASES
         1. Refer to Division 03 Section "Cast-in-Place Concrete" or "Miscellaneous Cast-in-Place Concrete."
         2. Concrete Bases: Anchor equipment to concrete base according to equipment manufacturer's written instructions at Project.

Construct concrete bases of dimensions indicated, but not less than 4 inches larger in both directions than supported unit.

* + - 1. ERECTION OF METAL SUPPORTS AND ANCHORAGES
         1. Refer to Division 05 Section 055000 "Metal Fabrications" for structural steel.
         2. Cut, fit, and place miscellaneous metal supports accurately in location, alignment, and elevation to support and anchor plumbing materials and equipment.
         3. Field Welding: Comply with AWS D1.1.
      2. GROUTING
         1. Mix and install grout for plumbing equipment base bearing surfaces, pump and other equipment base plates, and anchors.

END OF SECTION 220500