SECTION 220523 - GENERAL-DUTY VALVES FOR PLUMBING PIPING

1. GENERAL
	* + 1. RELATED DOCUMENTS
				1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.
			2. SUMMARY
				1. Section Includes:

Bronze ball valves.

Cast iron ball valves.

Iron, single-flange butterfly valves.

Iron, grooved-end butterfly valves.

Bronze lift check valves.

Bronze swing check valves.

Iron swing check valves.

Iron, grooved-end swing check valves.

Iron, center-guided check valves.

Bronze gate valves.

Iron gate valves.

* + - * 1. Related Sections:

Division 22 plumbing piping Sections for specialty valves applicable to those Sections only.

Division 22 Section "Identification for Plumbing Piping and Equipment" for valve tags and schedules.

Division 33 water distribution piping Sections for general-duty and specialty valves for site construction piping.

* + - 1. DEFINITIONS
				1. CWP: Cold working pressure.
				2. EPDM: Ethylene propylene copolymer rubber.
				3. NBR: Acrylonitrile-butadiene, Buna-N, or nitrile rubber.
				4. NRS: Nonrising stem.
				5. OS&Y: Outside screw and yoke.
				6. RS: Rising stem.
				7. SWP: Steam working pressure.
			2. ACTION SUBMITTALS
				1. Product Data: For each type of valve indicated.
			3. QUALITY ASSURANCE
				1. Source Limitations for Valves: Obtain each type of valve from single source from single manufacturer.
				2. ASME Compliance:

ASME B16.10 and ASME B16.34 for ferrous valve dimensions and design criteria.

ASME B31.1 for power piping valves.

ASME B31.9 for building services piping valves.

* + - * 1. NSF Compliance: NSF 61 for valve materials for potable-water service.
			1. DELIVERY, STORAGE, AND HANDLING

Information in this article is paraphrased from MSS.

* + - * 1. Prepare valves for shipping as follows:

Protect internal parts against rust and corrosion.

Protect threads, flange faces, grooves, and weld ends.

Set angle, gate, and globe valves closed to prevent rattling.

Set ball and plug valves open to minimize exposure of functional surfaces.

Set butterfly valves closed or slightly open.

Block check valves in either closed or open position.

* + - * 1. Use the following precautions during storage:

Maintain valve end protection.

Store valves indoors and maintain at higher than ambient dew point temperature. If outdoor storage is necessary, store valves off the ground in watertight enclosures.

* + - * 1. Use sling to handle large valves; rig sling to avoid damage to exposed parts. Do not use handwheels or stems as lifting or rigging points.
1. PRODUCTS
	* + 1. GENERAL REQUIREMENTS FOR VALVES

Plumbing valve applications specified in this Section are limited to NPS 12 (DN 300). Many valves specified are available in larger sizes.

* + - * 1. Refer to valve schedule articles for applications of valves.

Caution: Revise pressure ratings and insert temperature ratings in valve articles if valves with higher ratings are required. Valves larger than NPS 12 (DN 300) typically have a lower pressure rating than smaller valves. Verify pressure requirements for large valves.

* + - * 1. Valve Pressure and Temperature Ratings: Not less than indicated and as required for system pressures and temperatures.
				2. Valve Sizes: Same as upstream piping unless otherwise indicated.
				3. Valve Actuator Types:

Gear Actuator: For quarter-turn valves NPS 8 (DN 200) and larger.

Handwheel: For valves other than quarter-turn types.

Handlever: For quarter-turn valves NPS 6 (DN 150) and smaller.

Wrench: For plug valves with square heads. Furnish Owner with 1 wrench for every 10 plug valves, for each size square plug-valve head.

Chainwheel: Device for attachment to valve handwheel, stem, or other actuator; of size and with chain for mounting height, as indicated in the "Valve Installation" Article.

* + - * 1. Valves in Insulated Piping: With 2-inch (50-mm) stem extensions and the following features:

Gate Valves: With rising stem.

Ball Valves: With extended operating handle of non-thermal-conductive material, and protective sleeve that allows operation of valve without breaking the vapor seal or disturbing insulation.

Butterfly Valves: With extended neck.

* + - * 1. Valve-End Connections:

Flanged: With flanges according to ASME B16.1 for iron valves.

Grooved: With grooves according to AWWA C606.

Valve solder-joint connections are common in smaller sizes of plumbing piping. Soldering and brazing methods used to achieve required pressure-temperature ratings may damage internal valve parts. Special installation requirements for soldered valves may make threaded valves more cost-effective.

Caution: Use solder with melting point below 840 deg F (454 deg C) for angle, check, gate, and globe valves and below 421 deg F (216 deg C) for ball valves.

Solder Joint: With sockets according to ASME B16.18.

Threaded: With threads according to ASME B1.20.1.

* + - * 1. Valve Bypass and Drain Connections: MSS SP-45.
			1. BRONZE BALL VALVES

Retain one or more of eight paragraphs in this article if bronze ball valves are required. MSS SP-110 covers both brass and bronze, copper-alloy ball valves NPS 1/4 to NPS 4 (DN 8 to DN 100). See the Evaluations and manufacturers' catalogs before selecting either brass or bronze ball valves or including both.

Caution: Two-piece ball valves with a full or regular port are recommended for most services. One-piece ball valves have a reduced port and one fewer leak path. Three-piece ball valves are recommended if disassembly without removing valve from piping is required.

Where pressure drop is a concern, use full-port ball valves. For corrosive or high-temperature applications, use stainless-steel-trim ball valves.

* + - * 1. Two-Piece, Full-Port, Bronze Ball Valves with Bronze Trim:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Apollo Valves; Model #77C-100 or 77C-200.

Crane Co.; Crane Valve Group; Crane Valves; Model #9302 or 9302S.

Hammond Valve; Model #8501, 8301A or 8511, 8311A.

Milwaukee Valve Company; Model #BA-400 or BA-450.

NIBCO INC; Model #T585-70 or S585-70.

Description:

Standard: MSS SP-110.

SWP Rating: 150 psig (1035 kPa).

CWP Rating: 600 psig (4140 kPa).

Body Design: Two piece.

Body Material: Bronze.

Ends: Threaded.

Seats: PTFE or TFE.

Stem: Bronze.

Ball: Chrome-plated brass.

Port: Full.

* + - * 1. Two-Piece, Full-Port, Bronze Ball Valves with Stainless-Steel Trim:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Conbraco Industries, Inc.; Apollo Valves.

Crane Co.; Crane Valve Group; Crane Valves.

Hammond Valve.

Milwaukee Valve Company.

NIBCO INC.

Description:

Standard: MSS SP-110.

SWP Rating: 150 psig (1035 kPa).

CWP Rating: 600 psig (4140 kPa).

Body Design: Two piece.

Body Material: Bronze.

Ends: Threaded.

Seats: PTFE or TFE.

Stem: Stainless steel.

Ball: Stainless steel, vented.

Port: Full.

* + - 1. CAST IRON BALL VALVES
				1. Two-Piece, Full-Port, Cast Iron Ball Valves with Stainless-Steel Trim:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Conbraco Industries, Inc.; Apollo Valves; Model 6PLF (Lead Free)

Approved equal

Description:

Standard: MSS SP-72.

SWP Rating: 125 psig.

CWP Rating: 200 psig.

Body Design: Two piece.

Body Material: Class 125 Cast Iron.

Ends: Threaded.

Seats: PTFE .

Stem: Stainless steel.

Ball: Stainless steel, vented.

Port: Full.

* + - 1. IRON, SINGLE-FLANGE BUTTERFLY VALVES

Retain one or more of six paragraphs in this article if iron, single-flange butterfly valves are required. MSS SP-67 covers iron, single-flange butterfly valves NPS 1-1/2 to NPS 72 (DN 40 to DN 1800).

* + - * 1. 200 CWP, Iron, Single-Flange Butterfly Valves with EPDM Seat and Aluminum-Bronze Disc:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Conbraco Industries, Inc.; Apollo Valves.

Crane Co.; Crane Valve Group; Jenkins Valves.

Crane Co.; Crane Valve Group; Stockham Division.

Hammond Valve.

Milwaukee Valve Company.

NIBCO INC.

Description:

Standard: MSS SP-67, Type I.

CWP Rating: 200 psig (1380 kPa).

Body Design: Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

Body Material: ASTM A 126, cast iron or ASTM A 536, ductile iron.

Seat: EPDM.

Stem: One- or two-piece stainless steel.

Disc: Aluminum bronze.

* + - * 1. 200 CWP, Iron, Single-Flange Butterfly Valves with EPDM Seat and Ductile-Iron Disc:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Conbraco Industries, Inc.; Apollo Valves.

Crane Co.; Crane Valve Group; Center Line.

Crane Co.; Crane Valve Group; Stockham Division.

DeZurik Water Controls.

Hammond Valve.

Milwaukee Valve Company.

NIBCO INC.

Description:

Standard: MSS SP-67, Type I.

CWP Rating: 200 psig (1380 kPa).

Body Design: Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

Body Material: ASTM A 126, cast iron or ASTM A 536, ductile iron.

Seat: EPDM.

Stem: One- or two-piece stainless steel.

Disc: Nickel-plated or -coated ductile iron.

* + - * 1. 200 CWP, Iron, Single-Flange Butterfly Valves with EPDM Seat and Stainless-Steel Disc:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Conbraco Industries, Inc.; Apollo Valves.

Crane Co.; Crane Valve Group; Jenkins Valves.

Crane Co.; Crane Valve Group; Stockham Division.

DeZurik Water Controls.

Hammond Valve.

Milwaukee Valve Company.

NIBCO INC.

Description:

Standard: MSS SP-67, Type I.

CWP Rating: 200 psig (1380 kPa).

Body Design: Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

Body Material: ASTM A 126, cast iron or ASTM A 536, ductile iron.

Seat: EPDM.

Stem: One- or two-piece stainless steel.

Disc: Stainless steel.

* + - 1. IRON, GROOVED-END BUTTERFLY VALVES

Retain one or both paragraphs in this article if iron, grooved-end butterfly valves are required. MSS SP-67 covers iron, grooved-end butterfly valves NPS 1-1/2 to NPS 72 (DN 40 to DN 1800).

* + - * 1. 175 CWP, Iron, Grooved-End Butterfly Valves:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Shurjoint Piping Products.

Tyco; Grinnell Mechanical Products.

Victaulic Company.

Description:

Standard: MSS SP-67, Type I.

CWP Rating: 175 psig (1200 kPa).

Body Material: Coated, ductile iron.

Stem: Two-piece stainless steel.

Disc: Coated, ductile iron.

Seal: EPDM.

* + - * 1. 300 CWP, Iron, Grooved-End Butterfly Valves:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Anvil International, Inc.

Kennedy Valve; a division of McWane, Inc.

NIBCO INC.

Shurjoint Piping Products.

Tyco Fire Products LP; Grinnell Mechanical Products.

Victaulic Company.

Description:

Standard: MSS SP-67, Type I.

NPS 8 (DN 200) and Smaller CWP Rating: 300 psig (2070 kPa).

NPS 10 (DN 250) and Larger CWP Rating: 200 psig (1380 kPa).

Body Material: Coated, ductile iron.

Stem: Two-piece stainless steel.

Disc: Coated, ductile iron.

Seal: EPDM.

* + - 1. BRONZE LIFT CHECK VALVES

Retain one or both paragraphs in this article if bronze lift check valves are required. MSS SP-80 covers bronze lift check valves NPS 1/4 to NPS 3 (DN 8 to DN 80).

* + - * 1. Class 125, Lift Check Valves with Bronze Disc:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Crane Co.; Crane Valve Group; Crane Valves.

Crane Co.; Crane Valve Group; Jenkins Valves.

Crane Co.; Crane Valve Group; Stockham Division.

Description:

Standard: MSS SP-80, Type 1.

CWP Rating: 200 psig (1380 kPa).

Body Design: Vertical flow.

Body Material: ASTM B 61 or ASTM B 62, bronze.

Ends: Threaded.

Disc: Bronze.

* + - * 1. Class 125, Lift Check Valves with Nonmetallic Disc:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hammond Valve.

Milwaukee Valve Company.

NIBCO INC.

Apollo Valves by Conbraco Industries, Inc.

Description:

Standard: MSS SP-80, Type 2.

CWP Rating: 200 psig (1380 kPa).

Body Design: Vertical flow.

Body Material: ASTM B 61 or ASTM B 62, bronze.

Ends: Threaded.

Disc: NBR, PTFE, or TFE.

* + - 1. BRONZE SWING CHECK VALVES

Retain one or more of four paragraphs in this article if bronze swing check valves are required. MSS SP-80 covers bronze swing check valves NPS 1/4 to NPS 3 (DN 8 to DN 80).

* + - * 1. Class 125, Bronze Swing Check Valves with Bronze Disc:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Crane Co.; Crane Valve Group; Crane Valves.

Crane Co.; Crane Valve Group; Jenkins Valves.

Crane Co.; Crane Valve Group; Stockham Division.

Hammond Valve.

Milwaukee Valve Company.

NIBCO INC.

Apollo Valves by Conbraco Industries, Inc.

Description:

Standard: MSS SP-80, Type 3.

CWP Rating: 200 psig (1380 kPa).

Body Design: Horizontal flow.

Body Material: ASTM B 62, bronze.

Ends: Threaded.

Disc: Bronze.

* + - * 1. Class 125, Bronze Swing Check Valves with Nonmetallic Disc:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Crane Co.; Crane Valve Group; Crane Valves.

Crane Co.; Crane Valve Group; Jenkins Valves.

Crane Co.; Crane Valve Group; Stockham Division.

Hammond Valve.

Milwaukee Valve Company.

NIBCO INC.

Apollo Valves by Conbraco Industries, Inc.

Description:

Standard: MSS SP-80, Type 4.

CWP Rating: 200 psig (1380 kPa).

Body Design: Horizontal flow.

Body Material: ASTM B 62, bronze.

Ends: Threaded.

Disc: PTFE or TFE.

* + - 1. IRON SWING CHECK VALVES

Retain one or more of three paragraphs in this article if iron swing check valves are required. MSS SP-71 covers iron swing check valves NPS 2 to NPS 24 (DN 50 to DN 600).

* + - * 1. Class 125, Iron Swing Check Valves with Metal Seats:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Crane Co.; Crane Valve Group; Crane Valves.

Crane Co.; Crane Valve Group; Jenkins Valves.

Crane Co.; Crane Valve Group; Stockham Division.

Hammond Valve.

Milwaukee Valve Company.

NIBCO INC.

Apollo Valves by Conbraco Industries, Inc.

Description:

Standard: MSS SP-71, Type I.

CWP Rating: 200 psig (1380 kPa).

Body Design: Clear or full waterway.

Body Material: ASTM A 126, gray iron with bolted bonnet.

Ends: Flanged.

Trim: Bronze.

Gasket: Asbestos free.

* + - * 1. Class 125, Iron Swing Check Valves with Nonmetallic-to-Metal Seats:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Crane Co.; Crane Valve Group; Crane Valves.

Crane Co.; Crane Valve Group; Stockham Division.

Description:

Standard: MSS SP-71, Type I.

CWP Rating: 200 psig (1380 kPa).

Body Design: Clear or full waterway.

Body Material: ASTM A 126, gray iron with bolted bonnet.

Ends: Flanged.

Trim: Composition.

Seat Ring: Bronze.

Disc Holder: Bronze.

Disc: PTFE or TFE.

Gasket: Asbestos free.

* + - 1. IRON, GROOVED-END SWING CHECK VALVES

Retain this article if iron, grooved-end swing check valves are required. No standard for these valves was located. They are available in NPS 2 to NPS 12 (DN 50 to DN 300).

* + - * 1. 300 CWP, Iron, Grooved-End Swing Check Valves:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Anvil International, Inc.

Shurjoint Piping Products.

Tyco; Grinnell Mechanical Products.

Victaulic Company.

Description:

CWP Rating: 300 psig (2070 kPa).

Body Material: ASTM A 536, ductile iron.

Seal: EPDM.

Disc: Spring-operated, ductile iron or stainless steel.

* + - 1. IRON, CENTER-GUIDED CHECK VALVES

Retain one or more of 16 paragraphs in this article if iron, center-guided check valves are required. MSS SP-125 covers iron, center-guided check valves NPS 2 to NPS 42 (DN 50 to DN 1050).

* + - * 1. Class 125, Iron, Globe, Center-Guided Check Valves with Metal Seat:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hammond Valve.

Milwaukee Valve Company.

NIBCO INC.

Description:

Standard: MSS SP-125.

CWP Rating: 200 psig (1380 kPa).

Body Material: ASTM A 126, gray iron.

Style: Globe, spring loaded.

Ends: Flanged.

Seat: Bronze.

* + - * 1. Class 125, Iron, Globe, Center-Guided Check Valves with Resilient Seat:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Anvil International, Inc.

Hammond Valve.

Milwaukee Valve Company.

NIBCO INC.

Description:

Standard: MSS SP-125.

CWP Rating: 200 psig (1380 kPa).

Body Material: ASTM A 126, gray iron.

Style: Globe, spring loaded.

Ends: Flanged.

Seat: EPDM.

* + - 1. BRONZE GATE VALVES

Retain one or more of four paragraphs in this article if bronze gate valves are required. MSS SP-80 covers bronze gate valves NPS 1/4 to NPS 3 (DN 8 to DN 80).

* + - * 1. Class 125, RS Bronze Gate Valves:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Crane Co.; Crane Valve Group; Crane Valves.

Crane Co.; Crane Valve Group; Jenkins Valves.

Crane Co.; Crane Valve Group; Stockham Division.

Hammond Valve.

Milwaukee Valve Company.

NIBCO INC.

Apollo Valves by Conbraco Industries, Inc.

Description:

Standard: MSS SP-80, Type 2.

CWP Rating: 200 psig (1380 kPa).

Body Material: ASTM B 62, bronze with integral seat and screw-in bonnet.

Ends: Threaded or solder joint.

Stem: Bronze.

Disc: Solid wedge; bronze.

Packing: Asbestos free.

Handwheel: Malleable iron.

* + - 1. IRON GATE VALVES

Retain one or more of four paragraphs in this article if iron gate valves are required. MSS SP-70 covers iron gate valves NPS 2 to NPS 48 (DN 50 to DN 1200).

* + - * 1. Class 125, OS&Y, Iron Gate Valves:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Crane Co.; Crane Valve Group; Crane Valves.

Crane Co.; Crane Valve Group; Jenkins Valves.

Crane Co.; Crane Valve Group; Stockham Division.

Hammond Valve.

Milwaukee Valve Company.

NIBCO INC.

Apollo Valves by Conbraco Industries, Inc.

Description:

Standard: MSS SP-70, Type I.

CWP Rating: 200 psig (1380 kPa).

Body Material: ASTM A 126, gray iron with bolted bonnet.

Ends: Flanged.

Trim: Bronze.

Disc: Solid wedge.

Packing and Gasket: Asbestos free.

* + - 1. LUBRICATED PLUG VALVES

Retain one or more of eight paragraphs in this article if lubricated plug valves are required. MSS SP-78 covers lubricated plug valves NPS 1 to NPS 24 (DN 25 to DN 600).

* + - * 1. Class 125, Regular-Gland, Lubricated Plug Valves with Threaded Ends:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Nordstrom Valves, Inc.

Description:

Standard: MSS SP-78, Type II.

CWP Rating: 200 psig (1380 kPa).

Body Material: ASTM A 48/A 48M or ASTM A 126, cast iron with lubrication-sealing system.

Pattern: Regular or short.

Plug: Cast iron or bronze with sealant groove.

* + - * 1. Class 125, Cylindrical, Lubricated Plug Valves with Threaded Ends:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Homestead Valve; a division of Olson Technologies, Inc.

Milliken Valve Company.

Description:

Standard: MSS SP-78, Type IV.

CWP Rating: 200 psig (1380 kPa).

Body Material: ASTM A 48/A 48M or ASTM A 126, cast iron with lubrication-sealing system.

Pattern: Regular or short.

Plug: Cast iron or bronze with sealant groove.

* + - * 1. Class 125, Cylindrical, Lubricated Plug Valves with Flanged Ends:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Homestead Valve; a division of Olson Technologies, Inc.

Milliken Valve Company.

Description:

Standard: MSS SP-78, Type IV.

CWP Rating: 200 psig (1380 kPa).

Body Material: ASTM A 48/A 48M or ASTM A 126, cast iron with lubrication-sealing system.

Pattern: Regular or short.

Plug: Cast iron or bronze with sealant groove.

* + - 1. CHAINWHEELS
				1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Babbitt Steam Specialty Co.

Roto Hammer Industries.

Trumbull Industries.

* + - * 1. Description: Valve actuation assembly with sprocket rim, brackets, and chain.

Brackets: Type, number, size, and fasteners required to mount actuator on valve.

Attachment: For connection to butterfly valve stems.

Sprocket Rim with Chain Guides: Ductile or cast iron, of type and size required for valve.

Chain: Hot-dip, galvanized steel, of size required to fit sprocket rim.

1. EXECUTION
	* + 1. EXAMINATION
				1. Examine valve interior for cleanliness, freedom from foreign matter, and corrosion. Remove special packing materials, such as blocks, used to prevent disc movement during shipping and handling.
				2. Operate valves in positions from fully open to fully closed. Examine guides and seats made accessible by such operations.
				3. Examine threads on valve and mating pipe for form and cleanliness.
				4. Examine mating flange faces for conditions that might cause leakage. Check bolting for proper size, length, and material. Verify that gasket is of proper size, that its material composition is suitable for service, and that it is free from defects and damage.
				5. Do not attempt to repair defective valves; replace with new valves.
			2. VALVE INSTALLATION
				1. Install valves with unions or flanges at each piece of equipment arranged to allow service, maintenance, and equipment removal without system shutdown.
				2. Locate valves for easy access and provide separate support where necessary.
				3. Install valves in horizontal piping with stem at or above center of pipe.
				4. Install valves in position to allow full stem movement.
				5. Install chainwheels on operators for butterfly valves NPS 4 (DN 100) and larger and more than 96 inches (2400 mm) above floor. Extend chains to 60 inches (1520 mm) above finished floor.
				6. Install check valves for proper direction of flow and as follows:

Revise check valve installation requirements to suit Project; delete those not required.

Swing Check Valves: In horizontal position with hinge pin level.

Center-Guided Check Valves: In horizontal or vertical position, between flanges.

Lift Check Valves: With stem upright and plumb.

* + - 1. ADJUSTING
				1. Adjust or replace valve packing after piping systems have been tested and put into service but before final adjusting and balancing. Replace valves if persistent leaking occurs.
			2. GENERAL REQUIREMENTS FOR VALVE APPLICATIONS

Caution: Verify that valve classes and pressure and temperature ratings are adequate for system fluid. Repeat each category listing if necessary and insert required pressure range for each listing. Indicate location of each different pressure system on Drawings.

Retain and revise valve applications in paragraphs and schedules below. Coordinate with valves specified in Part 2.

Apollo 6PLF Ball valves are preferred for domestic water shut-off duty as they have proven to be compatible with MSU Water Quality. Confirm space is available for the larger size valves. Edit spec as required.

* + - * 1. If valve applications are not indicated, use the following:

Shutoff Service:

6” and smaller: Ball valves

8” and larger: Butterfly valves

Butterfly Valve Dead-End Service: Single-flange (lug) type.

Throttling Service: Globe valves.

Pump-Discharge Check Valves:

NPS 2 (DN 50) and Smaller: Bronze swing check valves with bronze or nonmetallic disc.

NPS 2-1/2 (DN 65) and Larger for Domestic Water: Iron swing check valves with lever and weight or with spring or iron, center-guided, metal or resilient-seat check valves.

NPS 2-1/2 (DN 65) and Larger for Sanitary Waste and Storm Drainage: Iron swing check valves with lever and weight or spring.

* + - * 1. If valves with specified SWP classes or CWP ratings are not available, the same types of valves with higher SWP classes or CWP ratings may be substituted.
				2. Select valves, except wafer types, with the following end connections:

For Copper Tubing, NPS 2 (DN 50) and Smaller: Threaded ends except where solder-joint valve-end option is indicated in valve schedules below.

For Copper Tubing, NPS 2-1/2 (DN 65) and Larger: Flanged ends.

For Steel Piping, NPS 2 (DN 50) and Smaller: Threaded ends.

For Steel Piping, NPS 2-1/2 (DN 65): Flanged ends.

For Grooved-End Copper Tubing and Steel Piping: Valve ends may be grooved.

* + - 1. LOW-PRESSURE, COMPRESSED-AIR VALVE SCHEDULE (150 PSIG (1035 kPa) OR LESS)
				1. Pipe NPS 2 (DN 50) and Smaller:

Retain first subparagraph below if solder-joint valve ends are permitted for this application.

Bronze Valves: May be provided with solder-joint ends instead of threaded ends.

Caution: No one-piece, reduced-port, brass ball valves with stainless-steel trim; three-piece, regular-port, brass ball valves with brass trim; or bronze ball valves with bronze trim are included in the Section Text. Retain brass or stainless-steel trim with brass ball valves, or bronze or stainless-steel trim with bronze ball valves.

Ball Valves: Two piece, full port, bronze with brass, bronze or stainless-steel trim.

Bronze Lift Check Valves: Class 125, bronze disc.

Bronze Swing Check Valves: Class 125, bronze disc.

* + - * 1. Pipe NPS 2-1/2 (DN 65) and Larger:

Iron, Single-Flange Butterfly Valves: 200 CWP, NBR seat, aluminum-bronze or ductile-iron disc.

Iron, Grooved-End Butterfly Valves: 175 CWP.

Iron Swing Check Valves: Class 125, metal seats.

Iron, Grooved-End Swing Check Valves: 300 CWP.

Iron, Center-Guided Check Valves: Class 125, globe, metal seat.

* + - 1. DOMESTIC, HOT- AND COLD-WATER VALVE SCHEDULE
				1. Pipe NPS 2 (DN 50) and Smaller:

Retain first subparagraph below if solder-joint valve ends are permitted for this application.

Bronze Valves: May be provided with solder-joint ends instead of threaded ends.

Ball Valves: Two piece, full port, bronze with brass, bronze or stainless-steel trim.

Bronze Swing Check Valves: Class 125, bronze disc.

* + - * 1. Pipe NPS 2-1/2 (DN 65) and Larger:

Iron, Single-Flange Butterfly Valves: 200 CWP, EPDM seat, aluminum-bronze or ductile-iron disc.

Iron, Grooved-End Butterfly Valves: 175 CWP.

Iron Swing Check Valves: Class 125, metal seats.

Iron, Grooved-End Swing Check Valves: 300 CWP.

Iron, Center-Guided Check Valves: Class 125, globe, metal seat.

Iron Gate Valves: Class 125, OS&Y.

* + - 1. SANITARY-WASTE AND STORM-DRAINAGE VALVE SCHEDULE
				1. Pipe NPS 2 (DN 50) and Smaller:

Retain first subparagraph below if solder-joint valve ends are permitted for this application.

Bronze Valves: May be provided with solder-joint ends instead of threaded ends.

Retain only valve types, in five subparagraphs below, required for Project.

Caution: No one-piece, reduced-port, brass ball valves with stainless-steel trim; three-piece, regular-port, brass ball valves with brass trim; or bronze ball valves with bronze trim are included in the Section Text. Retain brass or stainless-steel trim with brass ball valves, or bronze or stainless-steel trim with bronze ball valves.

Ball Valves: Two piece, full port, bronze with bronze trim.

Bronze Swing Check Valves: Class 125, bronze disc.

Bronze Gate Valves: Class 125, NRS.

Bronze Globe Valves: Class 125, bronze disc.

* + - * 1. Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): May be provided with threaded ends instead of flanged ends.

Retain only valve types, in seven subparagraphs below, required for Project.

Iron Ball Valves: Class 150.

Retain one or more of first three subparagraphs below and indicate location of each type on Drawings.

Iron Swing Check Valves: Class 125, metal seats.

Iron Swing Check Valves with Closure Control: Class 125, lever and spring.

Iron, Grooved-End Swing Check Valves: 300 CWP.

Iron Gate Valves: Class 125, NRS.

Iron Globe Valves: Class 125.

Lubricated Plug Valves: Class 125, regular gland, flanged.

END OF SECTION 220523