## Sheet1
MSU West Regional Chilled Water Plant - Summary of Phases 1-2-3 12/22/2023
PHASE 1
Buildings Served
|  | Building | Sq Ft | Tons | Present Cooling Source
|  | C14 - EDIC | 262500 | 1500 | Not yet constructed
|  | C20 - PACKAGING ADDITION | 64400 | 215 | Not yet constructed
|  | ENGINEERING BUILDING | 421497 | 1531 | Engineering CHW Loop
|  | COMM. ARTS AND SCIENCES | 262442 | 612 | Engineering CHW Loop
|  | ANTHONY HALL | 319754 | 1347 | Engineering CHW Loop
|  | PACKAGING | 56162 | 206 | Engineering CHW Loop
|  | FOOD SCIENCE | 120101 | 608 | Engineering CHW Loop
|  | NATURAL RESOURCES | 149972 | 395 | Engineering CHW Loop
|  | C-03 STUDENT RECREATION AND WELLNESS CENTER | 305000 | 987 | Not yet constructed
|  | Total Connected Loop Load | 1961828 | 7401
|  | Diversified Loop Load | 80% | 5920.8
Existing Loop Chillers and Cooling Towers to Remain Operational
|  | Location | Quantity | Tons Capacity
|  | Engineering - 1200 ton electric centrifugal | 2 | 2400
|  | Anthony Hall - 955 ton steam absorption | 2 | 1910
|  | Food Science - 620 ton steam absorption | 2 | 1240
Existing Loop Chillers and Cooling Towers to be Removed
|  | Location | Quantity | Tons Capacity
None
| New Chiller Plant Building Size (approx.) |  |  | 160'x125'
| New Chillers |  |  | Quantity | Tons Capacity
|  | 1000 ton electric centrifugal |  | 1 | 1000
|  | 2800 ton steam turbine centrifugal |  | 1 | 2800
|  | 2800 ton electric centrifugal |  | 0 | 0
|  | Total installed chiller capacity in WRCW plant |  | 2 | 3800
|  | Total Installed chiller capacity on WRCWP loop |  | 8 | 9350
| N-1 chiller capacity on WRCWP loop |  |  | 7 | 6550
| Chiller capacity on WRCWP loop if all absorption chillers failed but all centrifugal chillers operational |  |  | 4 | 6200
| Installed Chiller Capacity on WRCWP loop as % Diversified Load |  |  |  | 157.9%
| N-1 Chiller Capacity on WRCWP loop as % Diversified Load |  |  |  | 110.6%
| Chiller capacity on WRCWP loop as % Diversified Load if all absorption chillers failed but all centrifugal chillers operational |  |  |  | 104.7%
| Site Steam Piping |  |  | New 20" steam and 10" condensate services to plant through crawl tunnel. Connect steam service to both existing 24" steam service mains at Vault #210
| Net added campus summer steam load for cooling, cumulative through phase (lbs/hr) |  |  | Steam turbine chillers | 29000
|  |  |  | Absorption chillers | no change
|  |  |  | Total | 29000
| Site Chilled Water Piping |  |  | Extend site chilled water piping from WRCWP to Engineering Loop, to EDIC, to Student Recreation and Wellness Center and to northwest side of the intersection of Red Cedar Road and North Shaw Lane.
| Site Electrical |  |  | 1. Need a new electrical duct bank from ELE 1848 (Trowbridge Road, north of Railroad Crossing) to the south side of the WRCWP. 2. Requires a new 15kV circuit pair (H-11 & H-31) from T.B. Simon Power Plant to the new WRCWP building. MSU Cost: $1,472,000
| Net added campus summer electrical load for cooling, cumulative through phase (kW) |  |  | 1230
PHASE 2
Additional Buildings Served
|  | Building | Sq Ft | Tons | Present Cooling Source
|  | C20 - PACKAGING ADDITION | 64400 | 215 | Not yet constructed
|  | Additional Connected Load | 64400 | 215
|  | Total Connected Loop Load | 2026228 | 7616
|  | Diversified Loop Load | 80% | 6092.8
Existing Loop Chillers and Cooling Towers to Remain Operational
|  | Location | Quantity | Tons Capacity
|  | Engineering - 1200 ton electric centrifugal | 2 | 2400
|  | WRCWP - 1000 ton electric centrifugal | 1 | 1000
|  | WRCWP - 2800 ton steam turbine centrifugal | 1 | 2800
Existing Loop Chillers and Cooling Towers to be Removed
|  | Location | Quantity | Tons Capacity
|  | Anthony Hall - 955 ton steam absorption | 2 | 1910
|  | Food Science - 620 ton steam absorption | 2 | 1240
| New Chiller Plant Building Size (approx.) |  |  | No Change
| New Chillers |  |  | Quantity | Tons Capacity
|  | 1000 ton electric centrifugal |  | 0 | 0
|  | 2800 ton steam turbine centrifugal |  | 0 | 0
|  | 2800 ton electric centrifugal |  | 1 | 2800
|  | Total installed chiller capacity in WRCW plant |  | 3 | 6600
|  | Total Installed chiller capacity on WRCWP loop |  | 5 | 9000
| N-1 chiller capacity on WRCWP loop |  |  | 4 | 6200
| Installed Chiller Capacity on WRCWP loop as % Diversified Load |  |  |  | 147.7%
| N-1 Chiller Capacity on WRCWP loop as % Diversified Load |  |  |  | 101.8%
| Site Steam Piping |  |  | No Change
| Net added campus summer steam load for cooling, cumulative through phase (lbs/hr) |  |  | Steam turbine chillers | 29000
|  |  |  | Absorption chillers | -58905
|  |  |  | Total | -29905
| Site Chilled Water Piping |  |  | No Change
| Site Electrical |  |  | No Change
| Net added campus summer electrical load for cooling, cumulative through phase (kW) |  |  | 3326
PHASE 3
Additional Buildings Served
|  | Building | Sq Ft | Tons | Present Cooling Source
|  | WELLS HALL | 315886 | 980 | International Center/Wells Hall CHW Loop
|  | ERICKSON HALL | 219249 | 730 | International Center/Wells Hall CHW Loop
|  | INTERNATIONAL CENTER | 133524 | 564 | International Center/Wells Hall CHW Loop
|  | Additional Connected Load | 668659 | 2274
|  | Total Connected Loop Load | 2694887 | 9890
|  | Diversified Loop Load | 80% | 7912
Existing Loop Chillers and Cooling Towers to Remain Operational
|  | Location | Quantity | Tons Capacity
|  | Engineering - 1200 ton electric centrifugal | 2 | 2400
|  | WRCWP - 1000 ton electric centrifugal | 1 | 1000
|  | WRCWP - 2800 ton steam turbine centrifugal | 1 | 2800
|  | WRCWP - 2800 ton electric centrifugal | 1 | 2800
Existing Loop Chillers and Cooling Towers to be Removed
|  | Location | Quantity | Tons Capacity
|  | Wells Hall - 490 ton steam absorption | 2 | 980
|  | International Center - 800 ton steam absorption | 2 | 1600
| New Chiller Plant Building Size (approx.) |  |  | No Change
| New Chillers |  |  | Quantity | Tons Capacity
|  | 1000 ton electric centrifugal |  | 0 | 0
|  | 2800 ton steam turbine centrifugal |  | 1 | 2800
|  | 2800 ton electric centrifugal |  | 0 | 0
|  | Total installed chiller capacity in WRCWP |  | 3 | 9400
|  | Total Installed chiller capacity on WRCWP loop |  | 5 | 11800
| N-1 chiller capacity on WRCWP loop |  |  | 4 | 9000
| Installed Chiller Capacity on WRCWP loop as % Diversified Load |  |  |  | 157.9%
| N-1 Chiller Capacity on WRCWP loop as % Diversified Load |  |  |  | 113.8%
| Site Steam Piping |  |  | No Change
| Net added campus summer steam load for cooling, cumulative through phase (lbs/hr) |  |  | Steam turbine chillers | 58000
|  |  |  | Absorption chillers | -107151
|  |  |  | Total | -49151
| Site Chilled Water Piping |  |  | Extend site chilled water piping from northwest side of the intersection of Red Cedar Road and North Shaw Lane and connect to existing Wells Hall/International Center loop piping
| Site Electrical |  |  | No Change
| Net added campus summer electrical load for cooling, cumulative through phase (kW) |  |  | 3818